## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2023-12-23
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.22 | 0.22 |  |  | 0.22
2 |  |  | 0.26 | 0.24 |  |  | 0.26
3 |  |  | 0.3 | 0.3 | 0.3 | 0.28 | 0.3
4 | 0.28 |  |  | 0.28 | 0.28 | 0.28 | 0.28
5 |  |  |  | 0.26 | 0.26 | 0.26 | 0.26
6 | 0.24 | 0.24 |  |  | 0.24 | 0.24 | 0.24
7 |  |  |  | 0.26 | 0.24 | 0.24 | 0.26
8 | 0.24 |  |  | 0.24 | 0.24 | 0.24 | 0.24
9 | 0.24 | 0.24 |  | 0.26 | 0.22 | 0.22 | 0.26
10
11 |  |  | 0.22 | 0.22 | 0.22 | 0.24 | 0.24
12 | 0.24 | 0.24 |  | 0.26 | 0.24 | 0.24 | 0.26
13 | 0.26 | 0.26 |  | 0.28 | 0.24 | 0.24 | 0.28
14 | 0.24 |  | 0.3 | 0.22 | 0.22 | 0.22 | 0.3
15 |  |  | 0.26 | 0.22 | 0.22 | 0.22 | 0.26
16 | 0.22 |  |  | 0.22 | 0.22 | 0.22 | 0.22
17 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
18 |  |  | 0.22 | 0.22 | 0.2 | 0.2 | 0.22
19 |  |  | 0.22 | 0.22 | 0.22 | 0.22 | 0.22
20 |  |  | 0.2 | 0.22 | 0.22 |  | 0.22
21 |  |  | 0.24 | 0.22 | 0.22 | 0.22 | 0.24
22 | 0.22 |  |  | 0.22 | 0.22 | 0.22 | 0.22
23 |  |  |  | 0.22 | 0.22 |  | 0.22
24 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
25 | 0.26 |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.26
26 |  |  | 0.26 | 0.26 | 0.24 |  | 0.26
27 |  |  | 0.26 | 0.24 | 0.24 | 0.24 | 0.26
28 |  |  | 0.24 | 0.24 |  |  | 0.24
29 | 0.24 |  | 0.26 | 0.26 |  |  | 0.26
30 |  |  | 0.28 | 0.26 |  |  | 0.28
31 | 0.26 | 0.26 |  |  |  | 0.28 | 0.28
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2023-12-01 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 150 | 35 | 0 |  |  |  |  | 0.99 | 125 | 50 | 49.5 | 6.9 | 8 | 42.4277 | 116.6691 | 116.6691 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.06 | 130 | 50 | 53 | 6.9 | 8 | 42.7633 | 123.938 | 123.938 | yes
3 |  | 75 | 35 | 0 |  |  |  |  | 1.09 | 145 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.45 | 125 | 50 | 72.5 | 6.9 | 8 | 44.688 | 162.2361 | 162.2361 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.57 | 120 | 50 | 78.5 | 6.9 | 8 | 45.2993 | 173.2919 | 173.2919 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.59 | 160 | 50 | 79.5 | 6.9 | 8 | 45.4021 | 175.1022 | 175.1022 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.6 | 150 | 50 | 80 | 6.9 | 8 | 45.4536 | 176.0038 | 176.0038 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.62 | 180 | 50 | 81 | 6.9 | 8 | 45.5567 | 177.8003 | 177.8003 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.6 | 170 | 50 | 80 | 6.9 | 8 | 45.4536 | 176.0038 | 176.0038 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.65 | 175 | 50 | 82.5 | 6.8 | 8 | 44.1296 | 186.9494 | 186.9494 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.63 | 135 | 50 | 81.5 | 6.8 | 8 | 44.03 | 185.1011 | 185.1011 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.62 | 125 | 50 | 81 | 6.8 | 8 | 43.9803 | 184.1734 | 184.1734 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.6 | 140 | 50 | 80 | 6.8 | 8 | 43.8811 | 182.311 | 182.311 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.64 | 160 | 50 | 82 | 6.8 | 8 | 44.0798 | 186.0264 | 186.0264 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.63 | 185 | 50 | 81.5 | 6.8 | 8 | 44.03 | 185.1011 | 185.1011 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.64 | 180 | 50 | 82 | 6.8 | 8 | 44.0798 | 186.0264 | 186.0264 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.68 | 165 | 50 | 84 | 6.8 | 8 | 44.2795 | 189.7042 | 189.7042 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.69 | 190 | 50 | 84.5 | 6.8 | 8 | 44.3296 | 190.6177 | 190.6177 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.4 | 120 | 50 | 70 | 6.8 | 8 | 42.9023 | 163.1615 | 163.1615 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.43 | 155 | 50 | 71.5 | 6.8 | 8 | 43.0475 | 166.0955 | 166.0955 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.45 | 140 | 50 | 72.5 | 6.8 | 8 | 43.1447 | 168.0393 | 168.0393 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.5 | 180 | 50 | 75 | 6.8 | 7 | 46.3535 | 161.8001 | 161.8001 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.5 | 195 | 50 | 75 | 6.8 | 7 | 46.3535 | 161.8001 | 161.8001 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.46 | 190 | 50 | 73 | 6.8 | 7 | 46.1434 | 158.2023 | 158.2023 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.42 | 120 | 50 | 71 | 6.8 | 7 | 45.9344 | 154.5681 | 154.5681 | yes
26 |  | 150 | 35 | 0 |  |  |  |  | 1.2 | 160 | 50 | 60 | 6.8 | 7 | 44.8034 | 133.9184 | 133.9184 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.15 | 145 | 50 | 57.5 | 6.8 | 7 | 44.5507 | 129.0665 | 129.0665 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.16 | 180 | 50 | 58 | 6.8 | 7 | 44.6011 | 130.0417 | 130.0417 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.14 | 185 | 50 | 57 | 6.8 | 7 | 44.5003 | 128.089 | 128.089 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.16 | 120 | 50 | 58 | 6.8 | 7 | 44.6011 | 130.0417 | 130.0417 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.15 | 190 | 50 | 57.5 | 6.8 | 7 | 44.5507 | 129.0665 | 129.0665 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel