## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-01-24
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  | 0.26 | 0.26 |  |  |  | 0.26
2 | 0.24 |  |  |  | 0.24 |  | 0.24
3 | 0.24 |  |  | 0.24 | 0.24 |  | 0.24
4 |  |  | 0.26 |  | 0.24 |  | 0.26
5 |  |  | 0.24 | 0.28 |  |  | 0.28
6
7 | 0.24 | 0.24 | 0.24 |  |  |  | 0.24
8 |  | 0.24 | 0.24 |  |  |  | 0.24
9 |  | 0.22 |  |  | 0.26 |  | 0.26
10 |  |  |  |  | 0.28 |  | 0.28
11
12 |  |  |  | 0.3 |  |  | 0.3
13 | 0.28 |  |  | 0.28 | 0.26 |  | 0.28
14 |  |  | 0.24 | 0.26 | 0.26 |  | 0.26
15 |  |  | 0.26 |  |  |  | 0.26
16
17 |  |  | 0.3 | 0.28 | 0.26 |  | 0.3
18 |  |  | 0.24 | 0.24 |  |  | 0.24
19 | 0.24 |  |  |  | 0.22 | 0.22 | 0.24
20 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
21 |  |  | 0.22 | 0.22 | 0.24 |  | 0.24
22 |  | 0.22 | 0.22 |  |  | 0.22 | 0.22
23 |  |  |  | 0.22 | 0.22 |  | 0.22
24 |  |  | 0.22 | 0.22 |  |  | 0.22
25 | 0.22 | 0.22 | 0.22 |  |  | 0.22 | 0.22
26 |  |  |  | 0.24 | 0.22 |  | 0.24
27 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
28 |  |  | 0.22 | 0.24 | 0.24 |  | 0.24
29 |  |  | 0.22 | 0.22 |  |  | 0.22
30 |  | 0.22 | 0.22 |  |  | 0.22 | 0.222
31 |  |  | 0.22 | 0.22 |  |  | 0.22
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2024-01-24 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 150 | 35 | 0 |  |  |  |  | 1.16 | 145 | 50 | 58 | 6.8 | 7 | 44.6011 | 130.0417 | 130.0417 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.12 | 150 | 50 | 56 | 6.8 | 7 | 44.3998 | 126.1268 | 126.1268 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.16 | 170 | 50 | 58 | 6.9 | 7 | 46.2021 | 125.5353 | 125.5353 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.14 | 145 | 50 | 57 | 6.9 | 7 | 46.0974 | 123.6513 | 123.6513 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.12 | 140 | 50 | 56 | 6.9 | 7 | 45.9928 | 121.7581 | 121.7581 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.11 | 190 | 50 | 55.5 | 6.9 | 7 | 45.9407 | 120.8079 | 120.8079 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.1 | 185 | 50 | 55 | 6.9 | 7 | 45.8886 | 119.8555 | 119.8555 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.12 | 125 | 50 | 56 | 6.9 | 7 | 45.9928 | 121.7581 | 121.7581 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.1 | 160 | 50 | 55 | 6.9 | 7 | 45.8886 | 119.8555 | 119.8555 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.09 | 145 | 50 | 54.5 | 6.9 | 7 | 45.8366 | 118.9007 | 118.9007 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.11 | 130 | 50 | 55.5 | 6.9 | 7 | 45.9407 | 120.8079 | 120.8079 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.12 | 150 | 50 | 56 | 6.9 | 6 | 49.155 | 113.9254 | 113.9254 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.08 | 120 | 50 | 54 | 6.9 | 6 | 48.9309 | 110.3596 | 110.3596 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.05 | 185 | 50 | 52.5 | 6.9 | 6 | 48.7637 | 107.6622 | 107.6622 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.06 | 200 | 50 | 53 | 6.9 | 6 | 48.8193 | 108.5635 | 108.5635 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.04 | 150 | 50 | 52 | 6.9 | 6 | 48.708 | 106.7586 | 106.7586 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 6.9 | 6 | 48.6525 | 105.8528 | 105.8528 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.02 | 145 | 50 | 51 | 6.9 | 6 | 48.597 | 104.9448 | 104.9448 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.02 | 125 | 50 | 51 | 6.9 | 6 | 48.597 | 104.9448 | 104.9448 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.04 | 140 | 50 | 52 | 6.9 | 6 | 48.708 | 106.7586 | 106.7586 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.01 | 200 | 50 | 50.5 | 6.9 | 6 | 48.5416 | 104.0345 | 104.0345 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.02 | 210 | 50 | 51 | 6.9 | 6 | 48.597 | 104.9448 | 104.9448 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1 | 120 | 50 | 50 | 6.9 | 6 | 48.4862 | 103.1221 | 103.1221 | yes
24 |  |  | 35 | 0 |  |  |  |  | 0.99 | 180 | 50 | 49.5 | 6.9 | 6 | 48.431 | 102.2074 | 102.2074 | yes
25 |  |  | 35 | 0 |  |  |  |  | 0.98 | 195 | 50 | 49 | 6.9 | 6 | 48.3758 | 101.2904 | 101.2904 | yes
26 |  |  | 35 | 0 |  |  |  |  | 0.99 | 200 | 50 | 49.5 | 6.9 | 6 | 48.431 | 102.2074 | 102.2074 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.02 | 210 | 50 | 51 | 6.9 | 6 | 48.597 | 104.9448 | 104.9448 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.04 | 120 | 50 | 52 | 7 | 6 | 50.472 | 103.0274 | 103.0274 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.02 | 135 | 50 | 51 | 7 | 6 | 50.3566 | 101.2778 | 101.2778 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.06 | 140 | 50 | 53 | 7 | 6 | 50.5877 | 104.7685 | 104.7685 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.03 | 110 | 50 | 51.5 | 7 | 6 | 50.4142 | 102.1537 | 102.1537 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel