## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-06-24
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.24 | 0.22 |  |  | 0.24
2 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
3 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
4 |  |  | 0.22 | 0.222 |  | 0.26 | 0.26
5 |  |  | 0.22 | 0.22 |  |  | 0.22
6 |  |  | 0.2 | 0.24 |  | 0.26 | 0.24
7 |  |  | 0.22 | 0.22 |  |  | 0.22
8 | 0.22 |  |  | 0.24 | 0.22 | 0.22 | 0.24
9 |  |  | 0.22 | 0.22 |  | 0.22 | 0.22
10 | 0.24 |  |  |  | 0.24 | 0.24 | 0.24
11 |  | 0.24 | 0.26 | 0.28 |  |  | 0.28
12
13 |  |  | 0.28 | 0.24 | 0.24 |  | 0.28
14 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
15 |  |  | 0.2 | 0.2 | 0.22 | 0.22 | 0.22
16 |  |  | 0.24 | 0.24 |  |  | 0.24
17 | 0.24 |  | 0.26 |  | 0.24 | 0.24 | 0.26
18 |  |  | 0.22 | 0.22 |  |  | 0.22
19 |  | 0.24 | 0.24 |  |  | 0.24 | 0.24
20 |  |  | 0.24 |  |  |  | 0.24
21 |  | 0.26 | 0.24 | 0.24 |  |  | 0.26
22 |  |  |  | 0.24 | 0.24 | 0.24 | 0.24
23 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
24
25 |  |  | 0.26 | 0.26 | 0.26 | 0.26 | 0.26
26 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
27 |  |  |  | 0.22 | 0.22 |  | 0.22
28 |  |  |  | 0.22 | 0.22 |  | 0.22
29 |  |  | 0.26 | 0.26 | 0.26 |  | 0.26
30 |  | 0.24 | 0.24 | 0.24 |  |  | 0.24
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2024-06-24 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
8
1 |  | 150 | 35 | 0 |  |  |  |  | 1.03 | 150 | 50 | 51.5 | 6.9 | 8 | 42.6191 | 120.8378 | 120.8378 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.02 | 180 | 50 | 51 | 6.9 | 8 | 42.5712 | 119.7994 | 119.7994 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.04 | 230 | 50 | 52 | 6.9 | 8 | 42.6671 | 121.8737 | 121.8737 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.09 | 190 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.08 | 185 | 50 | 54 | 6.9 | 8 | 42.8598 | 125.9923 | 125.9923 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.09 | 165 | 50 | 54.5 | 6.9 | 8 | 42.9081 | 127.0157 | 127.0157 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.1 | 180 | 50 | 55 | 6.9 | 8 | 42.9564 | 128.0367 | 128.0367 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.11 | 290 | 50 | 55.5 | 6.9 | 8 | 43.0049 | 129.0552 | 129.0552 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.19 | 230 | 50 | 59.5 | 6.9 | 8 | 43.3945 | 137.1142 | 137.1142 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.18 | 240 | 50 | 59 | 6.9 | 8 | 43.3456 | 136.1154 | 136.1154 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.19 | 160 | 50 | 59.5 | 7 | 8 | 44.9477 | 132.3762 | 132.3762 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.16 | 180 | 50 | 58 | 7 | 8 | 44.7953 | 129.4779 | 129.4779 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.17 | 175 | 50 | 58.5 | 7 | 8 | 44.846 | 130.4463 | 130.4463 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.2 | 135 | 50 | 60 | 7 | 8 | 44.9986 | 133.3375 | 133.3375 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.2 | 200 | 50 | 60 | 7 | 8 | 44.9986 | 133.3375 | 133.3375 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.18 | 210 | 50 | 59 | 7 | 8 | 44.8968 | 131.4124 | 131.4124 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.19 | 145 | 50 | 59.5 | 7 | 8 | 44.9477 | 132.3762 | 132.3762 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.21 | 190 | 50 | 60.5 | 7 | 8 | 45.0496 | 134.2965 | 134.2965 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.21 | 185 | 50 | 60.5 | 7 | 8 | 45.0496 | 134.2965 | 134.2965 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.19 | 160 | 50 | 59.5 | 6.9 | 8 | 43.3945 | 137.1142 | 137.1142 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.15 | 125 | 50 | 57.5 | 6.9 | 8 | 43.1992 | 133.1044 | 133.1044 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.16 | 250 | 50 | 58 | 6.9 | 8 | 43.2479 | 134.1105 | 134.1105 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.16 | 260 | 50 | 58 | 6.9 | 9 | 40.5017 | 143.204 | 143.204 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.18 | 200 | 50 | 59 | 6.9 | 9 | 40.5924 | 145.3473 | 145.3473 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.14 | 190 | 50 | 57 | 6.9 | 9 | 40.4111 | 141.0503 | 141.0503 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.16 | 195 | 50 | 58 | 6.9 | 9 | 40.5017 | 143.204 | 143.204 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.17 | 200 | 50 | 58.5 | 6.9 | 9 | 40.547 | 144.277 | 144.277 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.14 | 150 | 50 | 57 | 6.9 | 9 | 40.4111 | 141.0503 | 141.0503 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.13 | 210 | 50 | 56.5 | 6.9 | 9 | 40.3659 | 139.9695 | 139.9695 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.18 | 240 | 50 | 59 | 6.9 | 9 | 40.5924 | 145.3473 | 145.3473 | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel