## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | clackamas
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-10-24
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.28 | 0.26 |  |  | 0.28
2 | 0.26 |  | 0.26 | 0.26 |  |  | 0.26
3 |  |  | 0.26 | 0.24 |  |  | 0.26
4 |  |  | 0.24 | 0.24 |  |  | 0.24
5 |  |  | 0.24 | 0.24 |  | 0.24 | 0.24
6 |  |  | 0.24 | 0.24 |  |  | 0.24
7
8 |  |  | 0.22 | 0.22 | 0.2 |  | 0.22
9 |  |  | 0.24 | 0.24 |  |  | 0.24
10 | 0.26 |  |  |  | 0.24 | 0.24 | 0.26
11 |  |  |  | 0.26 | 0.24 |  | 0.26
12 |  | 0.24 | 0.24 |  |  | 0.28 | 0.28
13 |  |  | 0.26 | 0.26 | 0.26 |  | 0.26
14 |  |  | 0.24 | 0.24 |  |  | 0.24
15 |  |  | 0.24 |  |  | 0.24 | 0.24
16 |  |  | 0.28 | 0.24 |  |  | 0.28
17 | 0.3 | [5 empty] | 0.3
18 |  |  | 0.28 | 0.28 | 0.24 |  | 0.28
19 |  |  | 0.24 | 0.24 | 0.26 |  | 0.26
20 |  |  | 0.24 | 0.26 | 0.26 |  | 0.26
21 |  |  | 0.26 | 0.26 |  |  | 0.26
22 | 0.24 |  |  |  | 0.26 | 0.26 | 0.26
23 |  |  | 0.26 | 0.26 |  |  | 0.26
24 |  |  | 0.28 | 0.26 |  |  | 0.28
25 |  |  |  | 0.24 | 0.24 |  | 0.24
26 |  |  | 0.24 | 0.26 | 0.28 |  | 0.28
27
28 |  |  | 0.28 | 0.28 | 0.3 | 0.3 | 0.3
29 |  |  | 0.24 | 0.24 | 0.26 |  | 0.26
30 |  |  | 0.28 | 0.28 |  |  | 0.28
31 | 0.28 |  |  |  | 0.28 | 0.26 | 0.28
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2024-10-24 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 220 | 35 | 0 |  |  |  |  | 1.09 | 200 | 50 | 54.5 | 7 | 10 | 38.9806 | 139.8132 | 139.8132 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.12 | 150 | 50 | 56 | 7 | 10 | 39.1111 | 143.1818 | 143.1818 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.11 | 125 | 50 | 55.5 | 7 | 10 | 39.0676 | 142.0616 | 142.0616 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.14 | 145 | 50 | 57 | 7 | 10 | 39.1984 | 145.4141 | 145.4141 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.13 | 190 | 50 | 56.5 | 7 | 10 | 39.1547 | 144.2993 | 144.2993 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.15 | 225 | 50 | 57.5 | 7 | 10 | 39.2421 | 146.5262 | 146.5262 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.1 | 140 | 50 | 55 | 7 | 10 | 39.024 | 140.9388 | 140.9388 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.09 | 165 | 50 | 54.5 | 7 | 10 | 38.9806 | 139.8132 | 139.8132 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.08 | 130 | 50 | 54 | 7 | 10 | 38.9372 | 138.6849 | 138.6849 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.06 | 150 | 50 | 53 | 7 | 10 | 38.8505 | 136.4202 | 136.4202 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.09 | 160 | 50 | 54.5 | 6.9 | 10 | 37.6551 | 144.7349 | 144.7349 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.11 | 200 | 50 | 55.5 | 6.9 | 10 | 37.7387 | 147.0639 | 147.0639 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.15 | 180 | 50 | 57.5 | 6.9 | 10 | 37.9066 | 151.6885 | 151.6885 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.2 | 160 | 50 | 60 | 6.9 | 10 | 38.1177 | 157.4072 | 157.4072 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.09 | 150 | 50 | 54.5 | 6.9 | 10 | 37.6551 | 144.7349 | 144.7349 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.15 | 155 | 50 | 57.5 | 6.9 | 10 | 37.9066 | 151.6885 | 151.6885 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.13 | 130 | 50 | 56.5 | 6.9 | 10 | 37.8226 | 149.3818 | 149.3818 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.06 | 145 | 50 | 53 | 6.9 | 10 | 37.53 | 141.2205 | 141.2205 | yes
19 |  |  | 35 | 0 |  |  |  |  | 1.09 | 190 | 50 | 54.5 | 6.9 | 10 | 37.6551 | 144.7349 | 144.7349 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.09 | 155 | 50 | 54.5 | 6.9 | 10 | 37.6551 | 144.7349 | 144.7349 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.06 | 170 | 50 | 53 | 6.9 | 10 | 37.53 | 141.2205 | 141.2205 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.02 | 165 | 50 | 51 | 6.9 | 9 | 39.8726 | 127.9075 | 127.9075 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.06 | 155 | 50 | 53 | 7 | 9 | 41.4718 | 127.7978 | 127.7978 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.03 | 160 | 50 | 51.5 | 7 | 9 | 41.3324 | 124.5996 | 124.5996 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.08 | 210 | 50 | 54 | 7 | 9 | 41.565 | 129.9171 | 129.9171 | yes
26 |  |  | 35 | 0 |  |  |  |  | 0.99 | 195 | 50 | 49.5 | 7 | 9 | 41.1474 | 120.2992 | 120.2992 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.06 | 180 | 50 | 53 | 7 | 9 | 41.4718 | 127.7978 | 127.7978 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.02 | 160 | 50 | 51 | 7 | 9 | 41.2861 | 123.5284 | 123.5284 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.08 | 150 | 50 | 54 | 7 | 9 | 41.565 | 129.9171 | 129.9171 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.04 | 135 | 50 | 52 | 7 | 9 | 41.3788 | 125.6682 | 125.6682 | yes
31 |  |  | 35 | 0 |  |  |  |  | 1.05 | 140 | 50 | 52.5 | 7 | 9 | 41.4252 | 126.7343 | 126.7343 | yes
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel