## Turbidity
OHA - Drinking Water Program -Turbidity Monitoring Report Form | [6 empty] | County: | CLACKAMAS
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2024-11-24
System Name: | Colton Water District |  |  | ID#: 41 | 00202 |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 |  |  | 0.26 | 0.26 | 0.24 |  | 0.26
2 |  |  | 0.24 | 0.24 | 0.24 | 0.244 | 0.24
3 |  |  | 0.26 | 0.24 | 0.24 |  | 0.26
4 |  |  | 0.22 | 0.22 | 0.22 |  | 0.22
5 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
6 |  |  | 0.22 | 0.22 | 0.2 |  | 0.22
7 |  | 0.22 | 0.2 |  |  |  | 0.22
8 |  | .
9 |  |  | 0.2 | 0.22 | 0.22 | 0.22 | 0.22
10 |  |  | 0.22 | 0.24 |  |  | 0.24
11 | 0.22 |  |  | 0.22 | 0.22 |  | 0.22
12 |  | 0.28 |  |  | 0.24 | 0.24 | 0.28
13 |  |  | 0.3 | 0.28 | 0.26 |  | 0.24
14 |  |  | 0.22 | 0.24 |  |  | 0.24
15 |  |  |  | 0.24 | 0.24 | 0.24 | 0.24
16 |  |  | 0.24 | 0.22 | 0.22 |  | 0.24
17 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
18
19 |  |  | 0.28 | 0.22 | 0.22 | 0.2 | 0.28
20 |  |  | 0.24 | 0.22 | 0.22 |  | 0.24
21 | 0.2 | 0.22 |  |  | 0.22 | 0.22 | 0.22
22 |  |  | 0.2 | 0.2 | 0.2 |  | 0.2
23 |  |  | 0.28 | 0.28 | 0.26 |  | 0.28
24 |  |  | 0.2 | 0.22 |  | 0.24 | 0.24
25 |  |  | 0.2 | 0.2 |  |  | 0.2
26 | 0.24 | 0.2 |  | 0.22 | 0.22 |  | 0.24
27 |  |  | 0.24 | 0.24 | 0.24 | 0.24 | 0.24
28 |  |  | 0.26 | 0.24 |  | 0.26 | 0.26
29 | 0.26 |  |  | 0.24 | 0.26 |  | 0.26
30 |  |  | 0.28 | 0.28 | 0.28 |  | 0.28
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 0.3 NTU? |  |  |  | yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 1 NTU? |  |  |  | yes | yes |  | yes
All turbidity readings < IFE2 triggers? |  |  |  | yes
Peter Dostert 6574
1 Including continuous NTU data, if applicable. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))

## CTs
| OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | OHA - Drinking Water Program - Surface Water Quality Data Form | [7 empty] | WTP- : | A
System Name: |  | Colton, City of |  |  |  | ID#: 41 |  | 00202 | Month/Year: | 2024-11-24 | [5 empty] | Giardia Log Inactivation Req'd: |  | 1
| Pre-Chlorination Segment | [7 empty] | Post-Chlorination Segment | [7 empty] | Total
Date / Time | Min. free chlorine residual after pre-chlorinatn ( C )3 | Peak hourly demand flow (Pre) | Contact time (Pre) (T) | Actual CTPre | Highest pH (Pre) | Lowest temp (Pre) | Required CTPre (Total) | Percent log inactivation achieved (Pre) | Min. free chlorine residual after post-chlorinatn ( C )3 | Peak hourly demand flow (Post) | Contact time (Post) (T) | Actual CTPost | Highest pH (Post) | Lowest temp (Post) | Required CTPost (Total) | Percent log inactivation achieved (Post)4 | Total percent of required log inactivation achieved | CT met?3
| [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [ppm or mg/L] | [GPM] | [minutes] | C X T |  | [° C] | formula | [%] | [%] | Yes/No
1 |  | 220 | 35 | 0 |  |  |  |  | 1.09 | 160 | 50 | 54.5 | 6.9 | 9 | 40.1857 | 135.6203 | 135.6203 | yes
2 |  |  | 35 | 0 |  |  |  |  | 1.1 | 190 | 50 | 55 | 6.9 | 9 | 40.2307 | 136.7115 | 136.7115 | yes
3 |  |  | 35 | 0 |  |  |  |  | 1.12 | 185 | 50 | 56 | 6.9 | 9 | 40.3208 | 138.8862 | 138.8862 | yes
4 |  |  | 35 | 0 |  |  |  |  | 1.12 | 140 | 50 | 56 | 6.9 | 8 | 43.0534 | 130.0712 | 130.0712 | yes
5 |  |  | 35 | 0 |  |  |  |  | 1.13 | 160 | 50 | 56.5 | 6.9 | 8 | 43.1019 | 131.0847 | 131.0847 | yes
6 |  |  | 35 | 0 |  |  |  |  | 1.13 | 140 | 50 | 56.5 | 6.9 | 8 | 43.1019 | 131.0847 | 131.0847 | yes
7 |  |  | 35 | 0 |  |  |  |  | 1.16 | 130 | 50 | 58 | 6.9 | 8 | 43.2479 | 134.1105 | 134.1105 | yes
8 |  |  | 35 | 0 |  |  |  |  | 1.14 | 145 | 50 | 57 | 6.9 | 8 | 43.1505 | 132.0958 | 132.0958 | yes
9 |  |  | 35 | 0 |  |  |  |  | 1.15 | 190 | 50 | 57.5 | 6.9 | 8 | 43.1992 | 133.1044 | 133.1044 | yes
10 |  |  | 35 | 0 |  |  |  |  | 1.18 | 125 | 50 | 59 | 6.9 | 8 | 43.3456 | 136.1154 | 136.1154 | yes
11 |  |  | 35 | 0 |  |  |  |  | 1.19 | 160 | 50 | 59.5 | 6.9 | 8 | 43.3945 | 137.1142 | 137.1142 | yes
12 |  |  | 35 | 0 |  |  |  |  | 1.2 | 145 | 50 | 60 | 6.9 | 8 | 43.4435 | 138.1106 | 138.1106 | yes
13 |  |  | 35 | 0 |  |  |  |  | 1.23 | 135 | 50 | 61.5 | 6.9 | 8 | 43.5907 | 141.085 | 141.085 | yes
14 |  |  | 35 | 0 |  |  |  |  | 1.24 | 150 | 50 | 62 | 7 | 8 | 45.2029 | 137.1593 | 137.1593 | yes
15 |  |  | 35 | 0 |  |  |  |  | 1.19 | 160 | 50 | 59.5 | 7 | 8 | 44.9477 | 132.3762 | 132.3762 | yes
16 |  |  | 35 | 0 |  |  |  |  | 1.18 | 190 | 50 | 59 | 7 | 8 | 44.8968 | 131.4124 | 131.4124 | yes
17 |  |  | 35 | 0 |  |  |  |  | 1.16 | 185 | 50 | 58 | 7 | 8 | 44.7953 | 129.4779 | 129.4779 | yes
18 |  |  | 35 | 0 |  |  |  |  | 1.18 | 150 | 50 | 59 | 7 | 8 | 44.8968 | 131.4124 | 131.4124 | yes
19 |  | 150 | 35 | 0 |  |  |  |  | 1.23 | 160 | 50 | 61.5 | 7 | 8 | 45.1517 | 136.2074 | 136.2074 | yes
20 |  |  | 35 | 0 |  |  |  |  | 1.2 | 155 | 50 | 60 | 7 | 7 | 48.0854 | 124.778 | 124.778 | yes
21 |  |  | 35 | 0 |  |  |  |  | 1.24 | 180 | 50 | 62 | 7 | 7 | 48.3052 | 128.3506 | 128.3506 | yes
22 |  |  | 35 | 0 |  |  |  |  | 1.23 | 130 | 50 | 61.5 | 7 | 7 | 48.2501 | 127.4608 | 127.4608 | yes
23 |  |  | 35 | 0 |  |  |  |  | 1.25 | 120 | 50 | 62.5 | 7 | 7 | 48.3603 | 129.2382 | 129.2382 | yes
24 |  |  | 35 | 0 |  |  |  |  | 1.19 | 150 | 50 | 59.5 | 7 | 7 | 48.0306 | 123.8793 | 123.8793 | yes
25 |  |  | 35 | 0 |  |  |  |  | 1.24 | 180 | 50 | 62 | 7 | 7 | 48.3052 | 128.3506 | 128.3506 | yes
26 |  |  | 35 | 0 |  |  |  |  | 1.22 | 185 | 50 | 61 | 7 | 7 | 48.1952 | 126.5687 | 126.5687 | yes
27 |  |  | 35 | 0 |  |  |  |  | 1.26 | 250 | 50 | 63 | 7 | 7 | 48.4155 | 130.1236 | 130.1236 | yes
28 |  |  | 35 | 0 |  |  |  |  | 1.25 | 155 | 50 | 62.5 | 7 | 7 | 48.3603 | 129.2382 | 129.2382 | yes
29 |  |  | 35 | 0 |  |  |  |  | 1.22 | 160 | 50 | 61 | 7 | 7 | 48.1952 | 126.5687 | 126.5687 | yes
30 |  |  | 35 | 0 |  |  |  |  | 1.23 | 125 | 50 | 61.5 | 7 | 7 | 48.2501 | 127.4608 | 127.4608 | yes
31 |  |  | 35 | 0 | [6 empty] | 50 | 0 | [5 empty] | yes
30
3 If Cl2 at entry point is less than 0.2 mg/L or CT not met, notify DWP within 24 hours. | [17 empty] | Revised August 2012
4 At least 0.5-log Giardia inactivation must occur after filtration. OAR 333-061-0050(4)(c)(D) | [17 empty] | I:\DWS\FS\WS Info\Clackamas\Colton - 00202\MORs\CT form template for Colton - excel