## January 2021
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Lane
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2021-01-01
System Name: | Creswell, City of |  |  | ID#: 4100246 |  |  | WTP : TP - | WTP-B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | off | off | 0.012 | 0.012 | 0.012 | 0.011 | 0.015
2 | 0.011 | off | off | 0.011 | 0.011 | 0.011 | 0.013
3 | off | off | off | 0.02 | 0.019 | 0.019 | 0.023
4 | 0.02 | 0.021 | 0.022 | off | off | 0.02 | 0.025
5 | 0.022 | 0.022 | 0.02 | off | 0.021 | off | 0.025
6 | 0.024 | 0.023 | off | off | off | 0.023 | 0.028
7 | off | off | off | 0.012 | 0.012 | off | 0.013
8 | off | off | off | 0.013 | 0.012 | 0.012 | 0.016
9 | off | off | off | 0.012 | 0.012 | 0.012 | 0.014
10 | off | off | off | 0.012 | 0.011 | 0.012 | 0.016
11 | off | 0.013 | 0.013 | off | off | 0.013 | 0.015
12 | 0.013 | off | off | off | 0.012 | 0.017 | 0.017
13 | 0.013 | 0.012 | off | off | off | 0.012 | 0.014
14 | 0.012 | 0.012 | off | off | 0.012 | 0.012 | 0.014
15 | off | off | off | 0.012 | 0.012 | 0.012 | 0.014
16 | off | off | off | 0.012 | 0.013 | 0.012 | 0.015
17 | 0.013 | off | off | 0.012 | 0.012 | 0.012 | 0.015
18 | 0.013 | off | off | 0.012 | 0.012 | 0.012 | 0.017
19 | 0.013 | off | off | off | 0.012 | 0.012 | 0.015
20 | 0.012 | 0.012 | off | 0.012 | off | off | 0.013
21 | off | off | 0.018 | 0.012 | 0.012 | off | 0.018
22 | off | off | off | 0.012 | 0.012 | 0.012 | 0.014
23 | off | off | off | 0.012 | 0.012 | 0.012 | 0.02
24 | 0.013 | off | off | 0.013 | 0.012 | 0.015 | 0.018
25 | off | off | 0.02 | off | 0.012 | 0.012 | 0.02
26 | 0.012 | 0.015 | off | off | off | 0.012 | 0.019
27 | 0.012 | 0.012 | off | off | off | off | 0.018
28 | off | off | off | 0.012 | 0.012 | off | 0.021
29 | off | off | off | 0.013 | 0.013 | 0.013 | 0.023
30 | off | off | off | 0.013 | 0.012 | 0.012 | 0.023
31 | 0.016 | off | off | off | 0.012 | 0.012 | 0.029
OHA - Drinking Water Program - Surface Water Quality Data Form |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings <1 NTU |  |  |  | (Yes) / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | (Yes) / No | (Yes) / No |  | (Yes) / No
[5 empty] | SIGNATURE: Mike Howard |  |  | 2021-02-04
[5 empty] | PHONE #: (541 ) 895-2531 Cell (541) 736-6015 |  |  | CERT #: T-5028
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : WTP-B
System Name: | Creswell, City of |  | ID#: 4100246 |  | Month/Year: | 2021-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.82 | 47 | 38.54 | 9 | 7.4 | 23.2273 | Yes | 1376 | 15.3127
2 | 0.91 | 47 | 42.77 | 8 | 7.4 | 25.0828 | Yes | 1063 | 17.6872
3 | 0.9 | 47 | 42.3 | 8 | 7.4 | 25.0541 | Yes | 841 | 17.2459
4 | 0.9 | 47 | 42.3 | 13 | 7.5 | 18.5148 | Yes | 805 | 23.7852
5 | 0.92 | 47 | 43.24 | 11 | 7.5 | 21.322 | Yes | 919 | 21.918
6 | 0.95 | 47 | 44.65 | 12 | 7.4 | 19.3536 | Yes | 1420 | 25.2964
7 | 0.96 | 47 | 45.12 | 9 | 7.4 | 23.6 | Yes | 914 | 21.52
8 | 0.96 | 47 | 45.12 | 9 | 7.4 | 23.6 | Yes | 1721 | 21.52
9 | 1 | 47 | 47 | 8 | 7.4 | 25.3426 | Yes | 840 | 21.6574
10 | 1.07 | 47 | 50.29 | 8 | 7.4 | 25.5467 | Yes | 929 | 24.7433
11 | 1.04 | 47 | 48.88 | 12 | 7.5 | 20.24 | Yes | 864 | 28.64
12 | 1.08 | 47 | 50.76 | 14 | 7.4 | 17.0404 | Yes | 846 | 33.7196
13 | 1.04 | 47 | 48.88 | 12 | 7.4 | 19.5486 | Yes | 1243 | 29.3314
14 | 1.02 | 47 | 47.94 | 9 | 7.4 | 23.7617 | Yes | 1757 | 24.1783
15 | 1.06 | 47 | 49.82 | 9 | 7.4 | 23.8702 | Yes | 845 | 25.9498
16 | 1.09 | 47 | 51.23 | 9 | 7.4 | 23.9519 | Yes | 800 | 27.2781
17 | 1.1 | 47 | 51.7 | 9 | 7.4 | 23.9792 | Yes | 963 | 27.7208
18 | 1.13 | 47 | 53.11 | 13 | 7.5 | 19.0042 | Yes | 1392 | 34.1058
19 | 1.15 | 47 | 54.05 | 12 | 7.4 | 19.7899 | Yes | 1455 | 34.2601
20 | 1.13 | 47 | 53.11 | 12 | 7.4 | 19.7458 | Yes | 1079 | 33.3642
21 | 1.09 | 47 | 51.23 | 10 | 7.4 | 22.4149 | Yes | 1816 | 28.8151
22 | 1.12 | 47 | 52.64 | 10 | 7.4 | 22.4911 | Yes | 843 | 30.1489
23 | 1.16 | 47 | 54.52 | 9 | 7.4 | 24.1438 | Yes | 1520 | 30.3762
24 | 1.06 | 47 | 49.82 | 8 | 7.4 | 25.5174 | Yes | 1045 | 24.3026
25 | 1.13 | 47 | 53.11 | 11 | 7.4 | 21.0807 | Yes | 1098 | 32.0293
26 | 1.13 | 47 | 53.11 | 11 | 7.6 | 22.6148 | Yes | 998 | 30.4952
27 | 1.19 | 47 | 55.93 | 11 | 7.4 | 21.2234 | Yes | 866 | 34.7066
28 | 1.06 | 47 | 49.82 | 9 | 7.4 | 23.8702 | Yes | 1589 | 25.9498
29 | 1.06 | 47 | 49.82 | 9 | 7.4 | 23.8702 | Yes | 1676 | 25.9498
30 | 1.16 | 47 | 54.52 | 9 | 7.4 | 24.1438 | Yes | 794 | 30.3762
31 | 1.17 | 47 | 54.99 | 10 | 7.3 | 21.8367 | Yes | 1182 | 33.1533
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | [6 empty] | Revised February 2012
PAGE 2 of 2
)'( | DHS
| Oregon Department |  |  |  |  | Water Quality Parameter Monitoring Form
| of Human Services |  |  |  | Lead & Copper Rule Corrosion Control
Day | pH | Alk | Phos | Sili | Y/N | <<Have | County: Lane Agency: REGION 2
1 | 7.4 | N/A | N/A | N/A | YES | minimums |  | ENTRY POINT
2 | 7.4 | N/A | N/A | N/A | YES | been met for |  | Entry Point: EP-B
3 | 7.4 | N/A | N/A | N/A | YES | this day? |  | PWS ID 4100246B
4 | 7.5 | N/A | N/A | N/A | YES |  | System Name: Creswell, City of
5 | 7.5 | N/A | N/A | N/A | YES |  | Sample period: | 2021-01-01
6 | 7.4 | N/A | N/A | N/A | YES |  |  | Month/year
7 | 7.4 | N/A | N/A | N/A | YES
8 | 7.4 | N/A | N/A | N/A | YES |  | Number of excursions during this month: __0___
9 | 7.4 | N/A | N/A | N/A | YES |  | (Over 9 excursions in 6 months is a violation.
10 | 7.4 | N/A | N/A | N/A | YES |  | Entry Point and Distribution excursions are
11 | 7.5 | N/A | N/A | N/A | YES |  | cumulative). An 'excursion' is any day in which the
12 | 7.4 | N/A | N/A | N/A | YES |  | water quality parameter(s) fall below the minimun
13 | 7.4 | N/A | N/A | N/A | YES |  | set by the State.
14 | 7.4 | N/A | N/A | N/A | YES
15 | 7.4 | N/A | N/A | N/A | YES
16 | 7.4 | N/A | N/A | N/A | YES
17 | 7.4 | N/A | N/A | N/A | YES |  | Reference: Minimun pH set on 11/3/2003 By John Potts.
18 | 7.5 | N/A | N/A | N/A | YES
19 | 7.4 | N/A | N/A | N/A | YES |  | Minimum Water Quality
20 | 7.4 | N/A | N/A | N/A | YES |  | Parameter(s) as set by State:
21 | 7.4 | N/A | N/A | N/A | YES
22 | 7.4 | N/A | N/A | N/A | YES |  | pH 7.1
23 | 7.4 | N/A | N/A | N/A | YES |  | Alk N/A | (Alkalinity)
24 | 7.4 | N/A | N/A | N/A | YES |  | PO4 N/A | (Orthophosphate)
25 | 7.4 | N/A | N/A | N/A | YES |  | Sili N/A | (Silicate)
26 | 7.6 | N/A | N/A | N/A | YES
27 | 7.4 | N/A | N/A | N/A | YES |  | Print Name: | Mike Howard
28 | 7.4 | N/A | N/A | N/A | YES
29 | 7.4 | N/A | N/A | N/A | YES |  | Signature: Mike Howard
30 | 7.4 | N/A | N/A | N/A | YES |  |  | 541-736-6015
31 | 7.3 | N/A | N/A | N/A | YES |  | 2021-02-04
(No=N=Excursion) |  |  | Total N's |  |  | Send to DWP within 10 days after end of sampling period
DHS, Drinking Water Program, PO Box 14350, Portland, OR 97293-0350
[5 empty] | Phone:(971) 673-0405 |  | Website: http://oregon.gov/DHS/ph/dwp/index.shtml