## Febuary 2021
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | County: | Lane
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | Febuary 2021
System Name: | Creswell, City of |  |  | ID#: 4100246 |  |  | WTP : TP - | WTP-B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | 0.013 | off | off | off | 0.017 | 0.012 | 0.023
2 | 0.012 | 0.012 | off | off | off | 0.013 | 0.023
3 | 0.012 | 0.012 | off | off | 0.016 | 0.012 | 0.022
4 | 0.012 | 0.013 | off | 0.012 | 0.013 | off | 0.023
5 | off | off | off | 0.012 | 0.012 | 0.012 | 0.023
6 | off | off | off | 0.013 | 0.013 | 0.013 | 0.022
7 | off | off | off | 0.013 | 0.013 | 0.014 | 0.022
8 | off | off | off | 0.013 | 0.012 | 0.012 | 0.022
9 | off | off | off | off | 0.012 | 0.012 | 0.023
10 | 0.013 | off | off | off | 0.017 | 0.012 | 0.022
11 | 0.012 | off | off | 0.012 | 0.012 | off | 0.018
12 | off | off | 0.012 | 0.012 | off | off | 0.02
13 | off | off | off | 0.013 | 0.013 | 0.013 | 0.024
14 | 0.014 | off | off | 0.013 | 0.014 | off | 0.019
15 | off | off | 0.015 | 0.013 | 0.013 | 0.013 | 0.021
16 | 0.017 | off | off | off | 0.016 | 0.012 | 0.02
17 | 0.013 | 0.013 | off | off | off | 0.013 | 0.021
18 | 0.013 | 0.013 | off | 0.013 | 0.014 | off | 0.017
19 | off | off | 0.014 | 0.013 | 0.013 | off | 0.019
20 | off | off | off | 0.013 | 0.013 | 0.014 | 0.017
21 | 0.015 | off | off | 0.013 | 0.013 | 0.014 | 0.017
22 | off | off | off | 0.014 | 0.013 | 0.013 | 0.019
23 | off | off | off | 0.013 | 0.013 | 0.012 | 0.018
24 | 0.013 | 0.016 | off | off | 0.016 | 0.013 | 0.018
25 | 0.013 | 0.013 | off | 0.012 | 0.015 | off | 0.016
26 | off | off | 0.014 | 0.014 | 0.013 | off | 0.02
27 | off | off | off | 0.013 | 0.013 | 0.013 | 0.019
28 | 0.013 | off | off | 0.012 | 0.012 | off | 0.017
29 | x | x | x | x | x | x | x
30 | x | x | x | x | x | x | x
31 | x | x | x | x | x | x | x
OHA - Drinking Water Program - Surface Water Quality Data Form |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings <1 NTU |  |  |  | (Yes) / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | (Yes) / No | (Yes) / No |  | (Yes) / No
[5 empty] | SIGNATURE: Mike Howard |  |  | 2021-03-04
[5 empty] | PHONE #: (541 ) 895-2531 Cell (541) 736-6015 |  |  | CERT #: T-5028
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP- : WTP-B
System Name: | Creswell, City of |  | ID#: 4100246 |  | Month/Year: | Febuary 2021 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.22 | 47 | 57.34 | 12 | 7.4 | 19.9452 | Yes | 1682 | 37.3948
2 | 1.21 | 47 | 56.87 | 13 | 7.4 | 18.4829 | Yes | 859 | 38.3871
3 | 1.26 | 47 | 59.22 | 12 | 7.4 | 20.0345 | Yes | 804 | 39.1855
4 | 1.28 | 47 | 60.16 | 9 | 7.4 | 24.4766 | Yes | 900 | 35.6834
5 | 1.28 | 47 | 60.16 | 9 | 7.4 | 24.4766 | Yes | 1594 | 35.6834
6 | 1.26 | 47 | 59.22 | 9 | 7.4 | 24.4208 | Yes | 855 | 34.7992
7 | 1.31 | 47 | 61.57 | 9 | 7.4 | 24.5606 | Yes | 1590 | 37.0094
8 | 1.32 | 47 | 62.04 | 8 | 7.4 | 26.2903 | Yes | 1187 | 35.7497
9 | 1.28 | 47 | 60.16 | 8 | 7.4 | 26.1698 | Yes | 968 | 33.9902
10 | 1.33 | 47 | 62.51 | 8 | 7.4 | 26.3206 | Yes | 1311 | 36.1894
11 | 1.32 | 47 | 62.04 | 8 | 7.4 | 26.2903 | Yes | 899 | 35.7497
12 | 1.33 | 47 | 62.51 | 8 | 7.4 | 26.3206 | Yes | 904 | 36.1894
13 | 1.26 | 47 | 59.22 | 8 | 7.4 | 26.1097 | Yes | 1640 | 33.1103
14 | 1.11 | 47 | 52.17 | 8 | 7.4 | 25.6641 | Yes | 1668 | 26.5059
15 | 1.12 | 47 | 52.64 | 9 | 7.5 | 24.9032 | Yes | 1460 | 27.7368
16 | 1.08 | 47 | 50.76 | 8 | 7.4 | 25.576 | Yes | 1630 | 25.184
17 | 1.06 | 47 | 49.82 | 9 | 7.5 | 24.733 | Yes | 1612 | 25.087
18 | 1.02 | 47 | 47.94 | 10 | 7.8 | 25.6253 | Yes | 1664 | 22.3147
19 | 1.02 | 47 | 47.94 | 9 | 7.4 | 23.7617 | Yes | 933 | 24.1783
20 | 0.96 | 47 | 45.12 | 9 | 7.4 | 23.6 | Yes | 1019 | 21.52
21 | 0.95 | 47 | 44.65 | 9 | 7.4 | 23.5732 | Yes | 1619 | 21.0768
22 | 0.92 | 47 | 43.24 | 13 | 7.5 | 18.5569 | Yes | 1131 | 24.6831
23 | 0.91 | 47 | 42.77 | 12 | 7.5 | 19.9479 | Yes | 1678 | 22.8221
24 | 0.91 | 47 | 42.77 | 11 | 7.5 | 21.2981 | Yes | 1237 | 21.4719
25 | 0.88 | 47 | 41.36 | 10 | 7.5 | 22.6733 | Yes | 1052 | 18.6867
26 | 0.89 | 47 | 41.83 | 9 | 7.4 | 23.4129 | Yes | 1718 | 18.4171
27 | 0.85 | 47 | 39.95 | 9 | 7.4 | 23.3066 | Yes | 1082 | 16.6434
28 | 0.88 | 47 | 41.36 | 9 | 7.4 | 23.3863 | Yes | 844 | 17.9737
29 | x | x | x | x | x | x | x | x | #VALUE!
30 | x | x | x | x | x | x | x | x | #VALUE!
31 | x | x | x | x | x | x | x | x | #VALUE!
3 If Cl2 at entry point < 0.2 mg/l or CT not met, DWP to be notified by end of next business day. | [6 empty] | Revised February 2012
PAGE 2 of 2
)'( | DHS
| Oregon Department |  |  |  |  | Water Quality Parameter Monitoring Form
| of Human Services |  |  |  | Lead & Copper Rule Corrosion Control
Day | pH | Alk | Phos | Sili | Y/N | <<Have | County: Lane Agency: REGION 2
1 | 7.4 | N/A | N/A | N/A | YES | minimums |  | ENTRY POINT
2 | 7.4 | N/A | N/A | N/A | YES | been met for |  | Entry Point: EP-B
3 | 7.4 | N/A | N/A | N/A | YES | this day? |  | PWS ID 4100246B
4 | 7.4 | N/A | N/A | N/A | YES |  | System Name: Creswell, City of
5 | 7.4 | N/A | N/A | N/A | YES |  | Sample period: | Febuary 2021
6 | 7.4 | N/A | N/A | N/A | YES |  |  | Month/year
7 | 7.4 | N/A | N/A | N/A | YES
8 | 7.4 | N/A | N/A | N/A | YES |  | Number of excursions during this month: __0___
9 | 7.4 | N/A | N/A | N/A | YES |  | (Over 9 excursions in 6 months is a violation.
10 | 7.4 | N/A | N/A | N/A | YES |  | Entry Point and Distribution excursions are
11 | 7.4 | N/A | N/A | N/A | YES |  | cumulative). An 'excursion' is any day in which the
12 | 7.4 | N/A | N/A | N/A | YES |  | water quality parameter(s) fall below the minimun
13 | 7.4 | N/A | N/A | N/A | YES |  | set by the State.
14 | 7.4 | N/A | N/A | N/A | YES
15 | 7.5 | N/A | N/A | N/A | YES
16 | 7.4 | N/A | N/A | N/A | YES
17 | 7.5 | N/A | N/A | N/A | YES |  | Reference: Minimun pH set on 11/3/2003 By John Potts.
18 | 7.8 | N/A | N/A | N/A | YES
19 | 7.4 | N/A | N/A | N/A | YES |  | Minimum Water Quality
20 | 7.4 | N/A | N/A | N/A | YES |  | Parameter(s) as set by State:
21 | 7.4 | N/A | N/A | N/A | YES
22 | 7.5 | N/A | N/A | N/A | YES |  | pH 7.1
23 | 7.5 | N/A | N/A | N/A | YES |  | Alk N/A | (Alkalinity)
24 | 7.5 | N/A | N/A | N/A | YES |  | PO4 N/A | (Orthophosphate)
25 | 7.5 | N/A | N/A | N/A | YES |  | Sili N/A | (Silicate)
26 | 7.4 | N/A | N/A | N/A | YES
27 | 7.4 | N/A | N/A | N/A | YES |  | Print Name: | Mike Howard
28 | 7.4 | N/A | N/A | N/A | YES
29 | x | N/A | N/A | N/A | x |  | Signature: Mike Howard
30 | x | N/A | N/A | N/A | x |  |  | 541-736-6015
31 | x | N/A | N/A | N/A | x |  | 2021-03-04
(No=N=Excursion) |  |  | Total N's |  | 0 | Send to DWP within 10 days after end of sampling period
DHS, Drinking Water Program, PO Box 14350, Portland, OR 97293-0350
[5 empty] | Phone:(971) 673-0405 |  | Website: http://oregon.gov/DHS/ph/dwp/index.shtml