## pg 1
Membrane Filter Monthly Operating Report |  |  |  |  | County: | Lane
| System Name: | City of Creswell |  |  | Month/Year: | Sept. 2025
| PWS ID#: 41 - | 00246 |  |  | Minimum test pressure applied ¦¦ req'd: | 22.0 psi // 17.5 psi
| Plant ID: WTP - | B | (e.g., "A")
[6 empty] | DIT = Direct Integrity Test on filter(s) [Yes, No, or "off" if all filters are offline] a | DIT Daily
|  |  | PDR = Pressure Decay Rate | PDRMax [psi/min] | LRC [log removal]
|  |  | LRC = Log Removal Credit | 0.3 | 4
Day | CFE Daily Turbidity [NTU] | Highest CFE♣ [NTU] | Highest IFE [NTU] (>15 min duration) | Highest PDR | Lowest LRVambient |  | [Y/N] or
|  |  |  | of day [psi/min] | of day [log removal] |  | "off"
1 | 0.017 | 0.02 | 0.021 | 0.05 | 4.54 |  | Y
2 | 0.017 | 0.021 | 0.022 | 0.06 | 4.54 |  | Y
3 | 0.018 | 0.019 | 0.022 | 0.06 | 4.54 |  | Y
4 | 0.017 | 0.018 | 0.022 | 0.05 | 4.54 |  | Y
5 | 0.019 | 0.024 | 0.084 | 0.05 | 4.55 |  | Y
6 | 0.017 | 0.026 | 0.08 | 0.05 | 4.58 |  | Y
7 | 0.017 | 0.024 | 0.047 | 0.05 | 4.62 |  | Y
8 | 0.018 | 0.021 | 0.054 | 0.05 | 4.57 |  | Y
9 | 0.017 | 0.019 | 0.022 | 0.04 | 4.86 |  | Y
10 | 0.018 | 0.021 | 0.03 | 0.04 | 4.61 |  | Y
11 | 0.017 | 0.019 | 0.02 | 0.04 | 4.69 |  | Y
12 | 0.017 | 0.041 | 0.133 | 0.04 | 4.6 |  | Y
13 | 0.016 | 0.035 | 0.047 | 0.04 | 4.71 |  | Y
14 | 0.017 | 0.019 | 0.028 | 0.04 | 4.66 |  | Y
15 | 0.02 | 0.021 | 0.014 | 0.04 | 4.66 |  | Y
16 | 0.02 | 0.02 | 0.015 | 0.05 | 4.58 |  | Y
17 | 0.02 | 0.021 | 0.015 | 0.05 | 4.58 |  | Y
18 | 0.02 | 0.02 | 0.023 | 0.05 | 4.62 |  | Y
19 | 0.02 | 0.028 | 0.042 | 0.05 | 4.61 |  | Y
20 | 0.02 | 0.026 | 0.045 | 0.05 | 4.66 |  | Y
21 | 0.02 | 0.026 | 0.066 | 0.05 | 4.58 |  | Y
22 | 0.019 | 0.021 | 0.022 | 0.06 | 4.54 |  | Y
23 | 0.019 | 0.021 | 0.021 | 0.06 | 4.54 |  | Y
24 | 0.019 | 0.021 | 0.021 | 0.05 | 4.55 |  | Y
25 | 0.02 | 0.021 | 0.027 | 0.05 | 4.56 |  | Y
26 | 0.02 | 0.027 | 0.044 | 0.05 | 4.54 |  | Y
27 | 0.02 | 0.023 | 0.025 | 0.06 | 4.56 |  | Y
28 | 0.02 | 0.03 | 0.058 | 0.06 | 4.52 |  | Y
29 | 0.02 | 0.031 | 0.121 | 0.05 | 4.56 |  | Y
30 | 0.02 | 0.022 | 0.026 | 0.05 | 4.56 |  | Y
31 | N/A | N/A | N/A | N/A | N/A |  | N/A
Compliance summary (operator to complete any blank fields)
95% of daily turbidity readings ≤ 1 NTU? [Y/N] |  | All turbidity readings ≤ 5 NTU? [Y/N] |  | All IFE turbidity readings ≤ 0.15 NTU? [Y/N] |  | Performance std met? [Y/N] | DIT Daily?
(PDR ≤ PDRMax, LRV ≥ LRC)
Yes |  | Yes |  | Yes |  | Yes | Yes
CT's met daily? (p. 2) |  | All Cl2 residual at EP ≥ 0.2 mg/L? |  | PDR < PDRMax? |  | LRVambient > LRC?
Yes |  | Yes |  | Yes |  | Yes
PRINTED NAME: |  | Sam Haynes |  |  | DATE: | 2025-09-01
SIGNATURE: |  | Sam Haynes |  |  | WT CERT #: | T-6414
Notes: Computer not set up for the new form |  |  |  |  | PHONE #: | 541-895-4044
p. 1 of 2

## pg 2
Disinfection Monthly Operating Report
| System Name: | City of Creswell
| PWS ID#: 41 - | 00246 | [5 empty] | 0.5 | b Log Inactivation
| Plant ID : WTP - | B | [6 empty] | Required via Disinfection
Day | Minimum Cl2 Residual at 1st User ( C ) ♦ | Contact Time | Actual CT | Temp | pH | Required CT | CT Met? ♦ | Peak Hourly | Notes
| [mg/L = ppm] | (T) | C x T | [° C] |  | (Formula) | [Yes / No] | Demand Flow
|  | [minutes] | (Formula) |  |  |  | (Formula) | [GPM] | (e.g. "Plant Off")
1 | 0.61 | 47 | 28.7 | 21 | 8.2 | 13.6 | YES | 1627
2 | 0.71 | 47 | 33.4 | 21 | 8.1 | 13.3 | YES | 1501
3 | 0.59 | 47 | 27.7 | 22 | 7.8 | 10.9 | YES | 1449
4 | 0.66 | 47 | 31 | 22 | 8 | 11.9 | YES | 1476
5 | 0.66 | 47 | 31 | 21 | 8 | 12.7 | YES | 1502
6 | 0.6 | 47 | 28.2 | 20 | 7.9 | 13 | YES | 1497
7 | 0.64 | 47 | 30.1 | 22 | 8.1 | 12.3 | YES | 1573
8 | 0.64 | 47 | 30.1 | 21 | 8 | 12.7 | YES | 1449
9 | 0.55 | 47 | 25.9 | 21 | 8.1 | 13 | YES | 1390
10 | 0.53 | 47 | 24.9 | 21 | 8.2 | 13.5 | YES | 1630
11 | 0.6 | 47 | 28.2 | 21 | 8 | 12.6 | YES | 1737
12 | 0.57 | 47 | 26.8 | 20 | 7.9 | 13 | YES | 1485
13 | 0.76 | 47 | 35.7 | 20 | 8.1 | 14.3 | YES | 1478
14 | 0.7 | 47 | 32.9 | 20 | 7.9 | 13.2 | YES | 1322
15 | 0.79 | 47 | 37.1 | 20 | 7.9 | 13.3 | YES | 1568
16 | 0.79 | 47 | 37.1 | 19 | 8.1 | 15.3 | YES | 1519
17 | 0.78 | 47 | 36.7 | 19 | 8.1 | 15.3 | YES | 1564
18 | 0.81 | 47 | 38.1 | 20 | 7.9 | 13.3 | YES | 1654
19 | 0.88 | 47 | 41.4 | 20 | 7.9 | 13.4 | YES | 1354
20 | 0.85 | 47 | 40 | 20 | 7.8 | 12.9 | YES | 1583
21 | 0.79 | 47 | 37.1 | 19 | 7.8 | 13.7 | YES | 1588
22 | 0.74 | 47 | 34.8 | 19 | 7.9 | 14.1 | YES | 1366
23 | 0.73 | 47 | 34.3 | 19 | 7.9 | 14.1 | YES | 1522
24 | 0.65 | 47 | 30.6 | 19 | 8 | 14.5 | YES | 1580
25 | 0.69 | 47 | 32.4 | 20 | 7.9 | 13.1 | YES | 1449
26 | 0.69 | 47 | 32.4 | 19 | 8 | 14.6 | YES | 1554
27 | 0.69 | 47 | 32.4 | 18 | 7.9 | 15 | YES | 1339
28 | 0.67 | 47 | 31.5 | 19 | 7.9 | 14 | YES | 1504
29 | 0.7 | 47 | 32.9 | 19 | 8 | 14.6 | YES | 1487
30 | 0.65 | 47 | 30.6 | 17 | 8 | 16.6 | YES | 1446
31 | N/A | N/A | #VALUE! | N/A | N/A | #VALUE! | #VALUE! | N/A | N/A
♦ If chlorine concentration at entry point < 0.2 mg/L, or CT not met, notify DWS within 24 hours.
Submit this monthly report by the 10th of following month by
| mail: | Drinking Water Services
PO Box 14350
Portland, OR 97293-0350
| email: | dwp.dmce@odhsoha.oregon.gov
| fax: | 971-673-0458 | [7 empty] | p. 2 of 2