## Turbidity and CT
OHA - Drinking Water Services - Surface Water Quality Data Form | [5 empty] | County: | LANE
Cartridge or Bag Filtration | [5 empty] | Month/Year: | 2025-08-25
System Name: | Alderwood Water Dev. Co. |  |  | ID#: 41 | 00304 | WTP ID: TP-
Day | PSI Before Filter | PSI After Filter | PSID | PSID When to Change Filter | Daily Turbidity Reading [NTU] | Highest Reading of the day 1 [NTU]
1 | 12 | 2 | 10 | 30 | 0.71
2 | 12 | 2 | 10 | 30 | 0.72
3 | 12 | 2 | 10 | 30 | 0.71
4 | 12 | 2 | 10 | 30 | 0.71
5 | 12 | 2 | 10 | 30 | 0.7
6 | 12 | 2 | 10 | 30 | 0.7
7 | 12 | 2 | 10 | 30 | 0.69
8 | 12 | 2 | 10 | 30 | 0.71
9 | 12 | 2 | 10 | 30 | 0.7
10 | 12 | 2 | 10 | 30 | 0.71
11 | 12 | 2 | 10 | 30 | 0.72
12 | 12 | 2 | 10 | 30 | 0.7
13 | 12 | 2 | 10 | 30 | 0.69
14 | 12 | 2 | 10 | 30 | 0.7
15 | 12 | 2 | 10 | 30 | 0.71
16 | 12 | 2 | 10 | 30 | 0.72
17 | 12 | 2 | 10 | 30 | 0.72
18 | 12 | 2 | 10 | 30 | 0.72
19 | 12 | 2 | 10 | 30 | 0.73
20 | 12 | 2 | 10 | 30 | 0.73
21 | 12 | 2 | 10 | 30 | 0.72
22 | 12 | 2 | 10 | 30 | 0.72
23 | 12 | 2 | 10 | 30 | 0.72
24 | 12 | 2 | 10 | 30 | 0.72
25 | 12 | 2 | 10 | 30 | 0.71
26 | 12 | 2 | 10 | 30 | 0.71
27 | 12 | 2 | 10 | 30 | 0.7
28 | 12 | 2 | 10 | 30 | 0.71
29 | 12 | 2 | 10 | 30 | 0.7
30 | 12 | 2 | 10 | 30 | 0.71
31 | 12 | 2 | 10 | 30 | 0.72
Cartridge & Bag Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? |  |  |  | Yes | CT's met everyday? (see back) | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes | Yes
Notes: PSI = pounds per square inch |  |  |  |  | PRINTED NAME: DANIEL REITZ
PSID = pounds per square inch difference (before filter - after filter) |  |  |  |  | SIGNATURE: |  | 2025-09-08
PSID When to Change Filter = look in manual for manufacturer's specifications when to change the filter, at what PSID. |  |  |  |  | PHONE #: ( 541 ) 342-1718 |  | CERT #: 6528
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in Daily Turbidity Reading column may not
correspond to continuous readings' maximum.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Alderwood Water Dev. Co. |  | ID#: 41 | 00304 | Month/Year: | 2025-08-25 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 2 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 2 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.27 | 44 | 55.88 | 17 | 7.3 | 27.4705 | YES
2 | 1.24 | 44 | 54.56 | 17 | 7.3 | 27.3765 | YES
3 | 1.22 | 44 | 53.68 | 17 | 7.5 | 29.4201 | YES
4 | 1.23 | 44 | 54.12 | 17 | 7.5 | 29.4536 | YES
5 | 1.25 | 44 | 55 | 17 | 7.5 | 29.5209 | YES
6 | 1.27 | 44 | 55.88 | 17 | 7.5 | 29.5883 | YES
7 | 1.24 | 44 | 54.56 | 17 | 7.5 | 29.4873 | YES
8 | 1.22 | 44 | 53.68 | 17 | 7.5 | 29.4201 | YES
9 | 1.24 | 44 | 54.56 | 17 | 7.5 | 29.4873 | YES
10 | 1.3 | 44 | 57.2 | 17 | 7.5 | 29.6898 | YES
11 | 1.28 | 44 | 56.32 | 17 | 7.5 | 29.6221 | YES
12 | 1.29 | 44 | 56.76 | 17 | 7.5 | 29.6559 | YES
13 | 1.27 | 44 | 55.88 | 17 | 7.5 | 29.5883 | YES
14 | 1.24 | 44 | 54.56 | 17 | 7.5 | 29.4873 | YES
15 | 1.22 | 44 | 53.68 | 17 | 7.5 | 29.4201 | YES
16 | 1.23 | 44 | 54.12 | 17 | 7.5 | 29.4536 | YES
17 | 1.25 | 44 | 55 | 17 | 7.5 | 29.5209 | YES
18 | 1.28 | 44 | 56.32 | 17 | 7.5 | 29.6221 | YES
19 | 1.3 | 44 | 57.2 | 17 | 7.4 | 28.6081 | YES
20 | 1.28 | 44 | 56.32 | 17 | 7.4 | 28.5429 | YES
21 | 1.29 | 44 | 56.76 | 17 | 7.4 | 28.5755 | YES
22 | 1.33 | 44 | 58.52 | 17 | 7.4 | 28.7063 | YES
23 | 1.35 | 44 | 59.4 | 17 | 7.4 | 28.7719 | YES
24 | 1.32 | 44 | 58.08 | 17 | 7.4 | 28.6735 | YES
25 | 1.3 | 44 | 57.2 | 17 | 7.4 | 28.6081 | YES
26 | 1.31 | 44 | 57.64 | 17 | 7.4 | 28.6408 | YES
27 | 1.28 | 44 | 56.32 | 17 | 7.2 | 26.4979 | YES
28 | 1.25 | 44 | 55 | 17 | 7.2 | 26.4071 | YES
29 | 1.23 | 44 | 54.12 | 17 | 7.2 | 26.3467 | YES
30 | 1.28 | 44 | 56.32 | 17 | 7.2 | 26.4979 | YES
31 | 1.33 | 44 | 58.52 | 17 | 7.2 | 26.6499 | YES
2 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2