## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | Lane
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2022-01-01
System Name: | Lowell, City Of |  |  | ID#: 4100492 |  |  | WTP : WTP - B
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.03 | 0.03 | 0.03 | 0.06 | 0.04 | 0.03 | 0.07
2 |  |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.15
3 |  |  |  | 0.05 | 0.03 | 0.03 | 0.2
4 |  |  | 0.03 | 0.03 | 0.03 |  | 0.04
5 |  |  | 0.06 | 0.05 | 0.03 | 0.03 | 0.06
6 |  |  | 0.03 | 0.03 | 0.03 |  | 0.04
7 |  |  | 0.11 | 0.05 | 0.03 | 0.03 | 0.06
8 | 0.03 | 0.03 | 0.04 | 0.04 | 0.05 | 0.05 | 0.06
9 |  |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
10 |  |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
11 |  |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
12 |  |  | 0.06 | 0.04 | 0.04 | 0.04 | 0.06
13 |  |  | 0.04 | 0.04 |  | 0.04 | 0.2
14 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
15 |  |  | 0.04 | 0.03 | 0.04 |  | 0.04
16 |  |  |  | 0.06 | 0.04 | 0.04 | 0.07
17 |  |  | 0.04 | 0.04 | 0.03 | 0.03 | 0.05
18 |  |  | 0.04 | 0.04 | 0.04 | 0.03 | 0.05
19 |  |  | 0.04 | 0.03 | 0.03 |  | 0.04
20 |  |  | 0.04 | 0.05 | 0.04 | 0.03 | 0.25
21 |  |  |  | 0.04 | 0.03 | 0.03 | 0.04
22 |  |  | 0.05 | 0.04 | 0.03 | 0.03 | 0.05 |  | .
23 |  |  | 0.04 | 0.03 | 0.03 | 0.03 | 0.04
24 |  |  | 0.04 | 0.04 | 0.07 | 0.05 | 0.09
25 |  |  | 0.04 | 0.04 | 0.03 | 0.03 | 0.05
26 |  |  | 0.04 | 0.05 | 0.05 | 0.04 | 0.06
27 |  |  |  | 0.04 |  | 0.03 | 0.04
28 |  |  |  | 0.04 | 0.07 |  | 0.07
29 |  |  |  | 0.05 | 0.04 | 0.04 | 0.06
30 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.04
31 |  |  |  | 0.04 | 0.03 |  | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Max Baker
[5 empty] | SIGNATURE: |  |  | DATE:
[5 empty] | PHONE #: 541-937-2776 |  |  | CERT #:08801FE
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(e)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - : WTP-B
System Name: | Lowell, City of |  | ID#: 4100492 |  | Month/Year: | 2022-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.03 | 66 | 67.98 | 9 | 6.9 | 19.9586 | Y | 155
2 | 0.98 | 66 | 64.68 | 9.5 | 6.98 | 19.7523 | Y | 155
3 | 1.01 | 81 | 81.81 | 9.8 | 7.06 | 19.9825 | Y | 155
4 | 1.01 | 81 | 81.81 | 9.1 | 7.12 | 21.363 | Y | 155
5 | 0.99 | 81 | 80.19 | 9.5 | 7.09 | 20.5462 | Y | 155
6 | 0.99 | 81 | 80.19 | 9.8 | 6.98 | 19.3919 | Y | 155
7 | 0.94 | 81 | 76.14 | 9 | 6.87 | 19.5543 | Y | 155
8 | 1 | 81 | 81 | 8.8 | 6.91 | 20.2235 | Y | 155
9 | 0.99 | 81 | 80.19 | 8.5 | 6.89 | 20.458 | Y | 155
10 | 0.91 | 81 | 73.71 | 9.8 | 6.93 | 18.8906 | Y | 155
11 | 0.85 | 81 | 68.85 | 9.7 | 6.95 | 19.0182 | Y | 155
12 | 0.88 | 81 | 71.28 | 9.5 | 6.97 | 19.4656 | Y | 155
13 | 0.81 | 81 | 65.61 | 9.7 | 6.98 | 19.1313 | Y | 155
14 | 0.92 | 81 | 74.52 | 8.8 | 6.76 | 19.0274 | Y | 155
15 | 0.88 | 81 | 71.28 | 8.7 | 6.78 | 19.1987 | Y | 155
16 | 0.85 | 81 | 68.85 | 8.7 | 6.88 | 19.8097 | Y | 155
17 | 0.9 | 81 | 72.9 | 8.9 | 6.9 | 19.7996 | Y | 155
18 | 0.88 | 81 | 71.28 | 8.8 | 6.79 | 19.1405 | Y | 155
19 | 0.82 | 81 | 66.42 | 9.3 | 6.92 | 19.2527 | Y | 155
20 | 0.81 | 81 | 65.61 | 8.9 | 6.75 | 18.6109 | Y | 155
21 | 0.81 | 81 | 65.61 | 8.8 | 6.89 | 19.6615 | Y | 155
22 | 0.85 | 81 | 68.85 | 8.6 | 6.97 | 20.5742 | Y | 155
23 | 0.87 | 81 | 70.47 | 9.1 | 6.88 | 19.3436 | Y | 155
24 | 0.85 | 81 | 68.85 | 8.3 | 6.91 | 20.5477 | Y | 155
25 | 0.85 | 81 | 68.85 | 8.7 | 6.9 | 19.9479 | Y | 155
26 | 0.85 | 81 | 68.85 | 9.4 | 6.89 | 18.9939 | Y | 155
27 | 0.84 | 81 | 68.04 | 8.8 | 6.99 | 20.4259 | Y | 155
28 | 0.83 | 81 | 67.23 | 8.5 | 6.89 | 20.0948 | Y | 155
29 | 0.81 | 81 | 65.61 | 8.7 | 6.9 | 19.8589 | Y | 155
30 | 0.83 | 81 | 67.23 | 8.7 | 6.95 | 20.2526 | Y | 155
31 | 0.78 | 81 | 63.18 | 8.5 | 7.02 | 20.9094 | Y | 155
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised October 2013
PAGE 2 of 2

## Start Stop Times
|  | Start Stop times for CxT | [24 empty] | Lowest Cl2 residul of the Day while Distribution pumps are ON! | Highest Finshed Turbidity of the Day While Distribution pumps are ON!
Month: | January |  | Year: | 2022
| Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | Start | Stop | mg/L | Time | NTUs
1st | 0:00 | 9:41 | 10:11 | 10:32 | 10:45 | 23:14 | [20 empty] | 1.03 | 12:31 | 0.07
2nd | 7:57 | 21:31 | [24 empty] | 0.98 | 15:07 | 0.15
3rd | 8:05 | 9:47 | 9:52 | 22:02 | [22 empty] | 1.01 | 9:47 | 0.2
4th | 7:07 | 19:28 | [24 empty] | 1.01 | 19:27 | 0.04
5th | 7:36 | 23:08 | [24 empty] | 0.99 | 9:45 | 0.06
6th | 7:05 | 17:19 | [24 empty] | 0.99 | 17:12 | 0.04
7th | 7:53 | 0:00 | [24 empty] | 0.94 | 9:28 | 0.06
8th | 0:00 | 12:17 | 15:25 | 23:36 | [22 empty] | 1 | 18:01 | 0.06
9th | 7:19 | 23:01 | [24 empty] | 0.99 | 9:29 | 0.04
10th | 7:44 | 22:17 | [24 empty] | 0.91 | 9:02 | 0.04
11th | 7:12 | 21:23 | [24 empty] | 0.85 | 7:32 | 0.04
12th | 7:53 | 20:23 | [24 empty] | 0.88 | 9:55 | 0.05
13th | 7:04 | 11:31 | 11:32 | 11:32 | 11:42 | 11:42 | 11:49 | 15:20 | 17:56 | 18:20 | 19:08 | 0:00 | [14 empty] | 0.81 | 11:51 | 0.2
14th | 0:00 | 22:43 | [24 empty] | 0.92 | 0:04 | 0.04
15th | 7:43 | 17:26 | 17:46 | 17:54 | [22 empty] | 0.88 | 17:04 | 0.04
16th | 8:33 | 21:22 | [24 empty] | 0.85 | 10:23 | 0.07
17th | 7:23 | 21:56 | [24 empty] | 0.9 | 10:05 | 0.05
18th | 7:40 | 22:00 | [24 empty] | 0.88 | 10:36 | 0.05
19th | 7:37 | 19:24 | 19:45 | 19:55 | [22 empty] | 0.82 | 8:04 | 0.04
20th | 7:36 | 17:03 | 17:04 | 23:13 | [22 empty] | 0.81 | 17:02 | 0.25
21st | 9:17 | 23:06 | [24 empty] | 0.81 | 12:13 | 0.04
22nd | 7:29 | 9:32 | 9:51 | 22:54 | [22 empty] | 0.85 | 7:51 | 0.05
23rd | 7:28 | 21:19 | [24 empty] | 0.87 | 7:55 | 0.04
24th | 7:33 | 14:31 | 15:09 | 22:17 | [22 empty] | 0.85 | 16:55 | 0.09
25th | 7:20 | 22:00 | [24 empty] | 0.85 | 8:46 | 0.05
26th | 7:13 | 9:05 | 10:25 | 10:33 | 10:57 | 22:18 | [20 empty] | 0.85 | 12:44 | 0.06
27th | 8:37 | 15:36 | 16:01 | 23:55 | [22 empty] | 0.84 | 8:57 | 0.04
28th | 9:16 | 13:55 | 14:18 | 16:43 | [22 empty] | 0.83 | 16:10 | 0.07
29th | 8:15 | 0:00 | [24 empty] | 0.81 | 8:35 | 0.06
30th | 0:00 | 9:24 | 10:41 | 23:35 | [22 empty] | 0.83 | 9:09 | 0.04
31st | 8:09 | 17:35 | [24 empty] | 0.78 | 10:29 | 0.04