## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | DOUGLAS
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2025-12-01
System Name: | TRI CITY JW&SA |  |  | ID#: 4100549 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
2 | OFF | OFF | OFF | OFF | 0.035 | 0.035 | 0.042
3 | 0.034 | 0.034 | OFF | OFF | OFF | OFF | 0.034
4 | OFF | OFF | OFF | OFF | OFF | OFF | 0.053
5 | 0.039 | 0.039 | 0.039 | 0.039 | 0.04 | OFF | 0.098
6 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
7 | OFF | OFF | OFF | OFF | 0.044 | 0.039 | 0.045
8 | 0.038 | 0.038 | 0.038 | OFF | OFF | OFF | 0.038
9 | OFF | OFF | OFF | OFF | 0.042 | 0.037 | 0.072
10 | 0.038 | 0.038 | OFF | OFF | OFF | OFF | 0.038
11 | OFF | OFF | OFF | OFF | OFF | 0.043 | 0.046
12 | 0.038 | 0.038 | 0.039 | 0.039 | OFF | OFF | 0.039
13 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | OFF | OFF | OFF | 0.044 | 0.04 | 0.039 | 0.048
15 | 0.039 | OFF | OFF | OFF | OFF | OFF | 0.039
16 | OFF | OFF | OFF | OFF | OFF | OFF | 0.051
17 | 0.043 | 0.038 | 0.038 | 0.039 | 0.038 | 0.038 | 0.043
18 | 0.038 | OFF | OFF | OFF | OFF | OFF | 0.038
19 | OFF | OFF | OFF | OFF | 0.054 | 0.038 | 0.057
20 | 0.039 | OFF | OFF | OFF | OFF | OFF | 0.039
21 | OFF | OFF | OFF | OFF | OFF | OFF | 0.047
22 | 0.038 | 0.038 | 0.038 | 0.038 | OFF | OFF | 0.038
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | OFF | OFF | 0.04 | 0.04 | 0.039 | 0.053
25 | 0.039 | OFF | OFF | OFF | OFF | OFF | 0.039
26 | OFF | OFF | OFF | OFF | OFF | 0.046 | 0.046
27 | 0.038 | 0.037 | 0.038 | 0.038 | OFF | OFF | 0.038
28 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
29 | OFF | OFF | OFF | 0.037 | 0.037 | 0.036 | 0.069
30 | 0.037 | 0.037 | OFF | OFF | OFF | OFF | 0.037
31 | OFF | OFF | OFF | 0.038 | 0.038 | 0.038 | 0.048
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: BRIAN KELLY
[5 empty] | SIGNATURE: BRIAN KELLY |  |  | DATE: 1-5-26
[5 empty] | PHONE #: ( 541 ) 580-2581 |  |  | CERT #: 8301/8441
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :A
System Name: | TRI CITY JW&SA |  | ID# 4100549 |  | Month/Year: | 2026-12-25 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | OFF | 60 | #VALUE! |  |  | #VALUE!
2 1:50 AM | 1.15 | 60 | 69 | 9.7 | 7.5 | 23.8495 | YES | 790
3 6:38 AM | 1.25 | 60 | 75 | 8.9 | 7.6 | 26.3715 | YES | 790
4 | OFF | 60 |  |  |  | #VALUE!
5 12:34 AM | 1.16 | 60 | 69.6 | 9.5 | 7.5 | 24.1967 | YES | 761
6 | OFF | 60 | #VALUE! |  |  | #VALUE! | #VALUE!
7 3:59 PM | 1.08 | 60 | 64.8 | 9.7 | 7.6 | 24.5147 | YES | 770
8 1:02 AM | 1.18 | 60 | 70.8 | 9.2 | 7.6 | 25.6394 | YES | 770
9 5:18 PM | 1.12 | 60 | 67.2 | 9..6 | 7.5 | 31 | YES | 779
10 6:00 AM | 1.18 | 60 | 70.8 | 9.8 | 7.5 | 23.7725 | YES | 779
11 9:22 PM | 1.2 | 60 | 72 | 10.3 | 7.5 | 23.0487 | YES | 767
12 12:37 PM | 1.14 | 60 | 68.4 | 9.9 | 7.5 | 23.5078 | YES | 767
13 | OFF | 60 | #VALUE! |  |  | #VALUE! | #VALUE!
14 11:33 AM | 1.32 | 60 | 79.2 | 10.3 | 7.5 | 23.365 | YES | 767
15 4:23 AM | 1.14 | 60 | 68.4 | 8.4 | 7.7 | 27.9137 | YES | 767
16 11:08 PM | 1.23 | 60 | 73.8 | 9.2 | 7.6 | 25.7869 | YES | 773
17 8:26 AM | 1.21 | 60 | 72.6 | 9.2 | 7.5 | 24.827 | YES | 773
18 4:30 AM | 1.17 | 60 | 70.2 | 9 | 7.6 | 25.9555 | YES | 773
19 3:42 PM | 1.34 | 60 | 80.4 | 9.5 | 7.5 | 24.6991 | YES | 773
20 2:00 AM | 1.13 | 60 | 67.8 | 9.7 | 7.3 | 22.1728 | YES | 773
21 10:03 PM | 1.17 | 60 | 70.2 | 10.1 | 7.2 | 20.9465 | YES | 765
22 8:14 AM | 1.13 | 60 | 67.8 | 8.6 | 7.3 | 23.8495 | YES | 765
23 | OFF | 60 | #VALUE! |  |  | #VALUE! | #VALUE!
24 10:21 AM | 1.53 | 60 | 91.8 | 9.5 | 7.3 | 23.511 | YES | 762
25 3:00 AM | 1.22 | 60 | 73.2 | 8.4 | 7.4 | 25.3031 | YES | 762
26 9:36 PM | 1.12 | 60 | 67.2 | 8.9 | 7.3 | 23.3523 | YES | 766
27 1:04 AM | 1.33 | 60 | 79.8 | 8.6 | 7.2 | 23.5496 | YES | 766
28 | OFF | 60 | #VALUE! |  |  | #VALUE! | #VALUE!
29 10:05 AM | 1.67 | 60 | 100.2 | 8.8 | 7.4 | 25.9388 | YES | 764
30 4:30 AM | 1.3 | 60 | 78 | 7.2 | 7.5 | 28.6939 | YES | 764
31 12:14 PM | 1.38 | 60 | 82.8 | 7.8 | 7.5 | 27.8107 | YES | 763
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2