## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | DOUGLAS
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-01-26
System Name: | TRI CITY JW&SA |  |  | ID#: 41 00549 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | 0.037 | OFF | OFF | OFF | OFF | OFF | 0.038
2 | OFF | OFF | OFF | OFF | OFF | OFF | 0.052
3 | 0.041 | 0.039 | 0.038 | 0.039 | 0.048 | OFF | 0.049
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | OFF | OFF | OFF | 0.048 | 0.04 | 0.037 | 0.054
6 | 0.037 | 0.037 | OFF | OFF | OFF | OFF | 0.037
7 | OFF | OFF | OFF | OFF | OFF | OFF | 0.045
8 | 0.039 | 0.037 | 0.037 | 0.037 | 0.036 | OFF | 0.039
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | OFF | OFF | OFF | OFF | 0.039 | 0.037 | 0.041
11 | 0.037 | 0.037 | 0.037 | OFF | OFF | OFF | 0.038
12 | OFF | OFF | OFF | OFF | OFF | OFF | 0.077
13 | 0.037 | 0.037 | 0.036 | 0.03 | 0.034 | OFF | 0.037
14 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
15 | OFF | OFF | OFF | 0.038 | 0.036 | 0.036 | 0.046
16 | 0.036 | OFF | OFF | OFF | OFF | OFF | 0.036
17 | OFF | OFF | OFF | OFF | 0.086 | 0.036 | 0.124
18 | 0.034 | 0.034 | 0.034 | OFF | OFF | OFF | 0.034
19 | OFF | OFF | OFF | OFF | OFF | OFF | 0.049
20 | 0.038 | 0.036 | 0.036 | 0.035 | 0.035 | OFF | 0.038
21 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
22 | OFF | OFF | OFF | 0.048 | 0.045 | 0.044 | 0.075
23 | 0.043 | 0.044 | OFF | OFF | OFF | OFF | 0.044
24 | OFF | OFF | OFF | OFF | OFF | OFF | 0.055
25 | 0.049 | 0.046 | 0.041 | 0.038 | 0.04 | OFF | 0.05
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | 0.069 | 0.041 | 0.076
28 | 0.039 | 0.039 | 0.042 | OFF | OFF | OFF | 0.046
29 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
30 | OFF | 0.046 | 0.041 | 0.41 | 0.039 | 0.038 | 0.055
31 | 0.039 | OFF | OFF | OFF | OFF | OFF | 0.04
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME:BRIAN KELLY
[5 empty] | SIGNATURE:BRIAN KELLY |  |  | DATE:2-3-26
[5 empty] | PHONE #: ( 541 )580-2581 |  |  | 8301/8441
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | TRI CITY JW&SA |  | ID#: 41 00549 |  | Month/Year: | 2026-01-26 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 12:30 AM | 1.37 | 60 | 82.2 | 6.9 | 7.5 | 29.521 | YES | 763
2 11:57 PM | 1.37 | 60 | 82.2 | 7.7 | 7.5 | 27.9666 | YES | 762
3 6:00 AM | 1.35 | 60 | 81 | 7.9 | 7.5 | 27.5284 | YES | 762
4 OFF
5 1:40 PM | 1.21 | 60 | 72.6 | 8.7 | 7.5 | 25.6712 | YES | 765
6 5:47 AM | 1.32 | 60 | 79.2 | 8.7 | 7.4 | 25.0862 | YES | 765
7 OFF
8 2:36 AM | 1.59 | 60 | 95.4 | 9 | 7.4 | 25.36 | YES | 769
9 OFF
10 2:01 PM | 1.57 | 60 | 94.2 | 8.4 | 7.5 | 27.3007 | YES | 758
11 12:05 AM | 1.3 | 60 | 78 | 7.3 | 7.5 | 28.5006 | YES | 758
12 11:02 PM | 1.52 | 60 | 91.2 | 7.6 | 7.5 | 28.6488 | YES | 765
13 8:43 AM | 1.31 | 60 | 78.6 | 6.6 | 7.4 | 28.8579 | YES | 765
14 OFF
15 12:23 PM | 1.55 | 60 | 93 | 7.1 | 7.5 | 29.7384 | YES | 775
16 2:00 AM | 1.3 | 60 | 78 | 6.3 | 7.5 | 30.4985 | YES | 775
17 4:52 PM | 1.41 | 60 | 84.6 | 6.9 | 7.5 | 29.6584 | YES | 768
18 7:55 AM | 1.2 | 60 | 72 | 5.9 | 7.5 | 30.9764 | YES | 768
19 11:50 PM | 1.53 | 60 | 91.8 | 6.4 | 7.5 | 31.1138 | YES | 763
20 9:05 AM | 1.2 | 60 | 72 | 5.8 | 7.5 | 31.1879 | YES | 763
21 OFF
22 1:05 PM | 1.46 | 60 | 87.6 | 6.5 | 7.6 | 31.784 | YES | 767
23 1:10 AM | 1.26 | 60 | 75.6 | 5.7 | 7.6 | 32.7915 | YES | 767
24 OFF
25 1:24 AM | 1.45 | 60 | 87 | 6.4 | 7.6 | 31.964 | YES | 766
26 OFF
27 4:09 PM | 1.55 | 60 | 93 | 6 | 7.6 | 33.2349 | YES | 758
28 9:30 AM | 1.3 | 60 | 78 | 4.8 | 7.7 | 36.3444 | YES | 758
29 OFF
30 4:45 AM | 1.62 | 60 | 97.2 | 5.8 | 7.6 | 33.97 | YES | 758
31 12:01 AM | 1.06 | 60 | 63.6 | 6.4 | 7.7 | 31.6715 | YES | 758
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2