## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | DOUGLAS
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-02-01
System Name: | TRI CITY WATER |  |  | 4100549 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | OFF | OFF | 0.044 | 0.06
2 | 0.043 | 0.038 | 0.042 | 0.038 | OFF | OFF | 0.043
3 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | OFF | OFF | 0.042 | 0.041 | 0.042 | 0.038 | 0.048
5 | 0.039 | OFF | OFF | OFF | OFF | OFF | 0.039
6 | OFF | OFF | OFF | OFF | 0.041 | 0.041 | 0.048
7 | 0.043 | 0.044 | OFF | OFF | OFF | OFF | 0.044
8 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
9 | OFF | 0.208 | 0.049 | 0.047 | 0.046 | OFF | 0.213
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | OFF | OFF | OFF | 0.051 | 0.044 | 0.054
12 | 0.046 | 0.046 | 0.046 | OFF | OFF | OFF | 0.046
13 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | OFF | OFF | 0.047 | 0.041 | 0.039 | 0.039 | 0.048
15 | 0.044 | OFF | OFF | OFF | OFF | OFF | 0.044
16 | OFF | OFF | OFF | OFF | OFF | 0.048 | 0.055
17 | 0.045 | 0.043 | 0.044 | 0.045 | OFF | OFF | 0.045
18 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | OFF | OFF | OFF | 0.055 | 0.045 | 0.044 | 0.059
20 | 0.044 | OFF | OFF | OFF | OFF | OFF | 0.044
21 | OFF | OFF | OFF | OFF | OFF | OFF | 0.087
22 | 0.047 | 0.045 | 0.045 | 0.045 | 0.044 | OFF | 0.047
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | OFF | OFF | 0.046 | 0.052 | 0.047 | 0.066
25 | 0.046 | 0.046 | OFF | OFF | OFF | OFF | 0.046
26 | OFF | OFF | OFF | OFF | OFF | OFF | 0.056
27 | 0.052 | 0.045 | 0.045 | 0.045 | 0.052 | OFF | 0.052
28 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
29
30
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: BRIAN KELLY
[5 empty] | SIGNATURE: BRIAN KELLY |  |  | 2026-03-09
[5 empty] | 541-580-2581 |  |  | 8441/8301
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | TRI CITY WATER |  | 4100459 |  | Month/Year: | 2026-02-26 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 7:31 AM | 1.27 | 60 | 76.2 | 6.9 | 7.7 | 31.3701 | YES | 757
2 10:17 AM | 1.4 | 60 | 84 | 7.1 | 7.6 | 30.3006 | YES | 757
3 OFF
4 9:13 AM | 1.54 | 60 | 92.4 | 7.9 | 7.5 | 28.1391 | YES | 762
5 3:30 AM | 1.09 | 60 | 65.4 | 7.9 | 7.7 | 28.7059 | YES | 762
6 3:56 PM | 1.47 | 60 | 88.2 | 8.4 | 7.6 | 27.9744 | YES | 766
7 2:00 AM | 1.09 | 60 | 65.4 | 7.9 | 7.6 | 27.6915 | YES | 766
8 OFF
9 2:18 AM | 1.53 | 60 | 91.8 | 8.1 | 7.5 | 27.7299 | YES | 764
10 OFF
11 4:02 PM | 1.89 | 60 | 113.4 | 8.7 | 7.1 | 24.0657 | YES | 761
8:27 | 1.19 | 60 | 71.4 | 7.9 | 7.3 | 25.161 | YES | 761
13 OFF
14 8:01 AM | 1.31 | 60 | 78.6 | 8.3 | 7.2 | 23.9694 | YES | 768
15 3:00 AM | 1.06 | 60 | 63.6 | 8.8 | 7.4 | 24.1901 | YES | 768
16 9:21 PM | 1.15 | 60 | 69 | 9.1 | 7.4 | 23.9563 | YES | 765
17 9:51 AM | 1.15 | 60 | 69 | 8.4 | 7.4 | 25.1012 | YES | 765
18 OFF
19 10:19 AM | 1.2 | 60 | 72 | 8.5 | 7.4 | 25.077 | YES | 758
20 2:03 AM | 0.94 | 60 | 56.4 | 7.5 | 7.3 | 25.1138 | YES | 758
21 9:56 PM | 1.07 | 60 | 64.2 | 7.8 | 7.4 | 25.8912 | YES | 762
22 3:35 PM | 1.03 | 60 | 61.8 | 7.5 | 7.4 | 26.2964 | YES | 762
23 OFF
24 12:59 PM | 1.08 | 60 | 64.8 | 8.3 | 7.4 | 25.0679 | YES | 753
25 1:00 AM | 1.68 | 60 | 100.8 | 9 | 7 | 22.2361 | YES | 753
26 11:39 PM | 1.39 | 60 | 83.4 | 9.5 | 7 | 20.8245 | YES | 764
27 9:22 AM | 1.14 | 60 | 68.4 | 9.1 | 7.1 | 21.5267 | YES | 764
28 OFF
29
30
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2