## Turbidity and CTs
OHA - Drinking Water Services -Turbidity Monitoring Report Form | [6 empty] | County: | DOUGLAS
Conventional or Direct Filtration | [6 empty] | Month/Year: | 2026-03-01
System Name: | TRI CITY WATER |  |  | ID#: 41 00549 |  |  | WTP : TP - | A
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the Day 1 [NTU]
1 | OFF | OFF | OFF | OFF | 0.059 | 0.045 | 0.06
2 | 0.04 | 0.04 | 0.045 | OFF | OFF | OFF | 0.05
3 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | 0.05 | 0.05 | 0.044 | 0.044 | OFF | OFF | 0.06
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | 0.22 | 0.073 | 0.05 | 0.04 | 0.236
7 | 0.04 | 0.04 | OFF | OFF | OFF | OFF | 0.04
8 | OFF | OFF | OFF | OFF | OFF | OFF | 0.06
9 | 0.05 | 0.044 | 0.04 | 0.04 | 0.04 | OFF | 0.05
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | OFF | OFF | OFF | 0.05 | 0.05 | 0.06
12 | 0.04 | 0.04 | 0.03 | OFF | OFF | OFF | 0.04
13 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | OFF | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04
15 | 0.03 | OFF | OFF | OFF | OFF | OFF | 0.03
16 | OFF | OFF | OFF | OFF | 0.03 | 0.03 | 0.04
17 | 0.03 | 0.03 | OFF | OFF | OFF | OFF | 0.03
18 | OFF | OFF | OFF | OFF | OFF | OFF | 0.04
19 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | OFF | 0.04
20 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
21 | OFF | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.05
22 | 0.03 | 0.03 | OFF | OFF | OFF | OFF | 0.03
23 | OFF | OFF | OFF | OFF | OFF | 0.03 | 0.04
24 | 0.03 | 0.03 | 0.03 | 0.03 | OFF | OFF | 0.03
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.04
27 | 0.03 | 0.03 | OFF | OFF | OFF | OFF | 0.03
28 | OFF | OFF | OFF | OFF | OFF | 0.035 | 0.04
29 | 0.03 | 0.03 | 0.03 | 0.03 | OFF | OFF | 0.03
30 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
31 | OFF | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of 4-hour turbidity readings ≤ 0.3 NTU? |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All 4-hour turbidity readings ≤ 1 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
All turbidity readings < IFE2 triggers |  |  |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: BRIAN KELLY
[5 empty] | SIGNATURE: BRIAN KELLY |  |  | DATE:4-1-26
[5 empty] | PHONE #: ( 541 ) 580-2581 |  |  | CERT #:8301/8441
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 IFE = Individ. Filter Effl. (333-061-0040(1)(d)(B&C))
PAGE 1 of 2
OHA - Drinking Water Program - Surface Water Quality Data Form | [6 empty] | WTP - :
System Name: | TRI CITY WATER |  | ID#: 41 00549 |  | Month/Year: | 2026-03-01 | Disinfection Giardia Log Inactive: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.26 | 60 | 75.6 | 9.7 | 7.1 | 20.9757 | YES | 766
2 | 1.11 | 60 | 66.6 | 9.8 | 7.2 | 21.2196 | YES | 766
3
4 | 1.21 | 60 | 72.6 | 10.2 | 7.1 | 20.1866 | YES | 772
5
6 | 1.18 | 60 | 70.8 | 10.3 | 7.1 | 19.988 | YES | 776
7 | 1.09 | 60 | 65.4 | 9.7 | 7.1 | 20.5792 | YES | 776
8
9 | 1.13 | 60 | 67.8 | 10.1 | 7.1 | 20.1379 | YES | 762
10
11 | 1.08 | 60 | 64.8 | 10.9 | 7.2 | 19.6798 | YES | 760
12 | 1.21 | 60 | 72.6 | 9.8 | 7.2 | 21.4598 | YES | 760
13
14 | 1.32 | 60 | 79.2 | 10.2 | 7.2 | 21.1633 | YES | 781
15 | 1.06 | 60 | 63.6 | 11 | 7.3 | 20.1983 | YES | 781
16 | 1.16 | 60 | 69.6 | 11.5 | 7.2 | 19.0962 | YES | 791
17 | 1.3 | 60 | 78 | 11.5 | 7.1 | 18.7367 | YES | 791
18 | 1.26 | 60 | 75.6 | 11.7 | 7 | 17.7925 | YES | 779
19 | 1.38 | 60 | 82.8 | 12.1 | 7 | 17.5715 | YES | 779
20
21 | 1.08 | 60 | 64.8 | 12.4 | 7 | 16.6803 | YES | 782
22 | 1.02 | 60 | 61.2 | 13.3 | 7.2 | 16.4679 | YES | 782
23 | 1.31 | 60 | 78.6 | 13.1 | 7.1 | 16.622 | YES | 785
24 | 1.34 | 60 | 80.4 | 12.6 | 7.1 | 17.2433 | YES | 785
25
26 | 1.09 | 60 | 65.4 | 12.3 | 7 | 16.8054 | YES | 782
27 | 1.08 | 60 | 64.8 | 12.2 | 7.1 | 17.4806 | YES | 782
28 | 1.07 | 60 | 64.2 | 12.5 | 7 | 16.2225 | YES | 785
29 | 1.16 | 60 | 69.6 | 12.4 | 7 | 16.8267 | YES | 785
30
31 | 1.09 | 60 | 65.4 | 12.3 | 7.2 | 17.9936 | YES | 789
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2