## Daily Readings
DAILY READING REPORT PANTHER CREEK WATER DISTRICT ID# 4100603-A | [7 empty] | Month _______________ | SEP |  | Year-- | 2023
|  | End of month reading |  | 15993.9 |  |  |  |  | Date: 9/30/2023
Date | Pumphouse | Gallons | Creek | Turbidity | 1st User | Salmon River | Pump House | Chlorine | Salmon River | Temp | PH | Rain | Init
| Meter Reading | Produced |  | Pump |  |  |  | 1st
| 00' |  |  | House |  |  |  | User
1 | 15995.3 | 1.4 | 0.23 | 0 | 0 | 0 | 1.71 | 2.12 | 0.68 | 12 | 7.33 | 0.5
2 | 16043.9 | 48.6 | 0.42 | 0 | 0 | 0 | 1.72 | 1.88 | 1.91 | 12.1 | 7.37 | 0
3 | 16097.9 | 54 | 0.34 | 0 | 0 | 0 | 1.58 | 1.04 | 1.27 | 12 | 7.36 | 0
4 | 16148.7 | 50.8 | 0.37 | 0 | 0 | 0 | 1.19 | 1.24 | 0.88 | 12.1 | 7.38 | 0.2
5 | 16195.4 | 46.7 | 0.46 | 0 | 0 | 0 | 1.35 | 1.64 | 1.25 | 12 | 7.23 | 0
6 | 16242.5 | 47.1 | 0.48 | 0 | 0 | 0 | 1.08 | 1.31 | 0.77 | 12.1 | 7.29 | 0
7 | 16290.9 | 48.4 | 0.28 | 0 | 0 | 0 | 1.56 | 1.91 | 0.58 | 12 | 7.25 | 0
8 | 16338.8 | 47.9 | 0.38 | 0 | 0 | 0 | 1.68 | 1.51 | 0.86 | 12.1 | 7.25 | 0
9 | 16388.2 | 49.4 | 0.21 | 0 | 0 | 0 | 1.59 | 1.21 | 1.24 | 12 | 7.26 | 0
10 | 16445.4 | 57.2 | 0.32 | 0 | 0 | 0 | 0.64 | 0.71 | 0.99 | 12.1 | 7.2 | 0
11 | 16514.4 | 69 | 0.7 | 0 | 0 | 0 | 0.93 | 0.97 | 0.74 | 12 | 7.23 | 0.1
12 | 16569.4 | 55 | 0.52 | 0 | 0 | 0 | 2.2 | 2.2 | 1.27 | 12.1 | 7.22 | 0
13 | 16624.5 | 55.1 | 0.17 | 0 | 0 | 0 | 1.89 | 2.2 | 1.25 | 12 | 7.37 | 0
14 | 16681 | 56.5 | 0.28 | 0 | 0 | 0 | 1.63 | 1.54 | 0.71 | 12.1 | 7.27 | 0
15 | 16748.3 | 67.3 | 0.4 | 0 | 0 | 0 | 1.62 | 1.29 | 1.58 | 12 | 7.27 | 0
16 | 16816.7 | 68.4 | 0.36 | 0 | 0 | 0 | 1.01 | 0.99 | 1.36 | 12.1 | 7.26 | 0
17 | 16884.9 | 68.2 | 0.38 | 0 | 0 | 0 | 0.57 | 0.91 | 1.22 | 12 | 7.27 | 0
18 | 16949.4 | 64.5 | 0.36 | 0 | 0 | 0 | 1.11 | 1.46 | 1.13 | 12.1 | 7.24 | 0
19 | 17012.4 | 63 | 0.38 | 0 | 0 | 0 | 1.73 | 1.72 | 0.58 | 12 | 7.3 | 0
20 | 17062.7 | 50.3 | 0.33 | 0 | 0 | 0 | 1.39 | 1.54 | 0.67 | 12.1 | 7.25 | 0
21 | 17105.9 | 43.2 | 0.36 | 0 | 0 | 0 | 1.72 | 2.09 | 1.69 | 12 | 7.33 | 0
22 | 17151.1 | 45.2 | 0.27 | 0 | 0 | 0 | 1.3 | 1.65 | 1.29 | 12.1 | 7.33 | 0
23 | 17201.7 | 50.6 | 0.39 | 0 | 0 | 0 | 0.8 | 1.07 | 1.29 | 12 | 7.33 | 0
24 | 17249.8 | 48.1 | 0.37 | 0 | 0 | 0 | 0.36 | 0.71 | 1.37 | 12.1 | 7.33 | 0.1
25 | 17308.8 | 59 | 1.27 | 0 | 0 | 0 | 0.1 | 0.72 | 0.72 | 12 | 7.27 | 0.6
26 | 17349.7 | 40.9 | 0.75 | 0 | 0 | 0 | 0.49 | 0.76 | 0.97 | 12.1 | 7.26 | 0.5
27 | 17396.3 | 46.6 | 1.14 | 0 | 0 | 0 | 0.75 | 0.57 | 1.06 | 12 | 7.25 | 0.5
28 | 17401.3 | 5 | 1.09 | 0 | 0 | 0 | 0.48 | 0.56 | 0.75 | 12.1 | 7.27 | 0.4
29 | 17494.1 | 92.8 | 0.42 | 0 | 0 | 0 | 1.19 | 1.36 | 0.81 | 12 | 7.44 | 0.5
30 | 17539.2 | 45.1 | 0.37 | 0 | 0 | 0 | 1.06 | 1.37 | 0.82 | 12.1 | 7.31 | 0
31 | 17539.2 | 0
| Monthly total produced | 1545.3
Page 1 of 8
MAX |  | 92.8 | 1.27 | 0 | 0 | 0 | 2.2 | 2.2 | 1.91 | 12.1 | 7.44 | 0.6
AVER |  | 49.8484 | 0.46 | 0 | 0 | 0 | 1.2143 | 1.3417 | 1.057 | 12.05 | 7.2907 | 0.11333
MIN |  | 0 | 0.17 | 0 | 0 | 0 | 0.1 | 0.56 | 0.58 | 12 | 7.2 | 0

## CHL
DAILY CHL REPORT PANTHER CREEK WATER DISTRICT ID# 4100603-A
Pump House End of Month Gallons ____________________
|  | Month | SEP | Year | 2023
Date | CI Gallons | CI | CI | H2O | CI Gallons
| Start | Used | Add | Add | End
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Page 2 of 8

## Quality Data Form
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Licolon
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | Date: 9/30/2023
System Name: |  |  |  | ID#: 41 | 00603 |  | WTP : TP -
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 |  |  | 0 |  |  |  | 0
2 |  |  | 0 |  |  |  | 0
3 |  |  | 0 |  |  |  | 0
4 |  |  | 0 |  |  |  | 0
5 |  |  | 0 |  |  |  | 0
6 |  |  | 0 |  |  |  | 0
7 |  |  | 0 |  |  |  | 0
8 |  |  | 0 |  |  |  | 0
9 |  |  | 0 |  |  |  | 0
10 |  |  | 0 |  |  |  | 0
11 |  |  | 0 |  |  |  | 0
12 |  |  | 0 |  |  |  | 0
13 |  |  | 0 |  |  |  | 0
14 |  |  | 0 |  |  |  | 0
15 |  |  | 0 |  |  |  | 0
16 |  |  | 0 |  |  |  | 0
17 |  |  | 0 |  |  |  | 0
18 |  |  | 0 |  |  |  | 0
19 |  |  | 0 |  |  |  | 0
20 |  |  | 0 |  |  |  | 0
21 |  |  | 0 |  |  |  | 0
22 |  |  | 0 |  |  |  | 0
23 |  |  | 0 |  |  |  | 0
24 |  |  | 0 |  |  |  | 0
25 |  |  | 0 |  |  |  | 0
26 |  |  | 0 |  |  |  | 0
27 |  |  | 0 |  |  |  | 0
28 |  |  | 0 |  |  |  | 0
29 |  |  | 0 |  |  |  | 0
30 |  |  | 0 |  |  |  | 0
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Martin Klinger
[5 empty] | SIGNATURE: |  |  | Date: 9/30/2023
[5 empty] | PHONE #: ( 541 ) 994-4548 |  |  | CERT #:7152
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :
System Name: | Panther Creek W D |  | ID#: 41 00603 |  | Month/Year: | Date: 9/30/2023 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 2.12 | 82.6 | 175.112 | 12 | 7.33 | 43 | YES | 0.097222
2 | 1.88 | 82.6 | 155.288 | 12.1 | 7.37 | 42 | YES | 3.375
3 | 1.04 | 82.6 | 85.904 | 12 | 7.36 | 39 | YES | 3.75
4 | 1.24 | 82.6 | 102.424 | 12.1 | 7.38 | 37 | YES | 3.5278
5 | 1.64 | 82.6 | 135.464 | 12 | 7.23 | 37 | YES | 3.2431
6 | 1.31 | 82.6 | 108.206 | 12.1 | 7.29 | 36 | YES | 3.2708
7 | 1.91 | 82.6 | 157.766 | 12 | 7.25 | 38 | YES | 3.3611
8 | 1.51 | 82.6 | 124.726 | 12.1 | 7.25 | 37 | YES | 3.3264
9 | 1.21 | 82.6 | 99.946 | 12 | 7.26 | 38 | YES | 3.4306
10 | 0.71 | 82.6 | 58.646 | 12.1 | 7.2 | 34 | YES | 3.9722
11 | 0.97 | 82.6 | 80.122 | 12 | 7.23 | 34 | YES | 4.7917
12 | 2.2 | 82.6 | 181.72 | 12.1 | 7.22 | 40 | YES | 3.8194
13 | 2.2 | 82.6 | 181.72 | 12 | 7.37 | 41 | YES | 3.8264
14 | 1.54 | 82.6 | 127.204 | 12.1 | 7.27 | 37 | YES | 3.9236
15 | 1.29 | 82.6 | 106.554 | 12 | 7.27 | 38 | YES | 4.6736
16 | 0.99 | 82.6 | 81.774 | 12.1 | 7.26 | 36 | YES | 4.75
17 | 0.91 | 82.6 | 75.166 | 12 | 7.27 | 34 | YES | 4.7361
18 | 1.46 | 82.6 | 120.596 | 12.1 | 7.24 | 37 | YES | 4.4792
19 | 1.72 | 82.6 | 142.072 | 12 | 7.3 | 39 | YES | 4.375
20 | 1.54 | 82.6 | 127.204 | 12.1 | 7.25 | 37 | YES | 3.4931
21 | 2.09 | 82.6 | 172.634 | 12 | 7.33 | 40 | YES | 3
22 | 1.65 | 82.6 | 136.29 | 12.1 | 7.33 | 41 | YES | 3.1389
23 | 1.07 | 82.6 | 88.382 | 12 | 7.33 | 39 | YES | 3.5139
24 | 0.71 | 82.6 | 58.646 | 12.1 | 7.33 | 35 | YES | 3.3403
25 | 0.72 | 82.6 | 59.472 | 12 | 7.27 | 34 | YES | 4.0972
26 | 0.76 | 82.6 | 62.776 | 12.1 | 7.26 | 34 | YES | 2.8403
27 | 0.57 | 82.6 | 47.082 | 12 | 7.25 | 33 | YES | 3.2361
28 | 0.56 | 82.6 | 46.256 | 12.1 | 7.27 | 34 | YES | 0.34722
29 | 1.36 | 82.6 | 112.336 | 12 | 7.44 | 41 | YES | 6.4444
30 | 1.37 | 82.6 | 113.162 | 12.1 | 7.31 | 39 | YES | 3.1319
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2

## Tank Levels
| PANTHER CREEK WATER DISTRICT ID# 4100603-A |  |  |  |  | Month | SEP | Year | 2023
Production Monitoring
Date | Reservoir Levels {{ FEET }} |  | Sand Filter Systems |  |  | End of shift Activities |  |  | Gates
Time | Steel Tank | Redwood | Filter 1 | Filter 2 | Flow meter | Reservoir Level | Pumphouse meter | Flow Meter | Chained
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Page 5 of 8

## Weeklyreadings
Panther Creek Water District ID# 4100603-A Month _Year |  |  | SEP | 2023
WEEKLY FIELD READINGS
| Sample Site | Date | Turbidity | Free Chlorine
| 98 N Westview Circle |  | 0 | 2.09
| 305 N Deerlane Drive |  | 0 | 2.1
1 | 465 N Fawn Dr | 2023-09-01 | 0 | 2.12
| 655 N Wayside Loop |  | 0 | 2.08
| 2345 N Silverside |  | 0 | 0.68
| 98 N Westview Circle |  | 0 | 1.49
| 305 N Deerlane Drive |  | 0 | 1.48
2 | 465 N Fawn Dr | 2023-09-08 | 0 | 1.51
| 655 N Wayside Loop |  | 0 | 1.47
| 2345 N Silverside |  | 0 | 0.86
| 98 N Westview Circle |  | 0 | 1.27
| 305 N Deerlane Drive |  | 0 | 1.28
3 | 465 N Fawn Dr | 2023-09-15 | 0 | 1.29
| 655 N Wayside Loop |  | 0 | 1.24
| 2345 N Silverside |  | 0 | 1.58
| 98 N Westview Circle |  | 0 | 1.63
| 305 N Deerlane Drive |  | 0 | 1.62
4 | 465 N Fawn Dr | 2023-09-22 | 0 | 1.65
| 655 N Wayside Loop |  | 0 | 1.63
| 2345 N Silverside |  | 0 | 1.29
| 98 N Westview Circle |  | 0 | 1.33
| 305 N Deerlane Drive |  | 0 | 1.32
5 | 465 N Fawn Dr | 2023-09-29 | 0 | 1.36
| 655 N Wayside Loop |  | 0 | 1.3
| 2345 N Silverside |  | 0 | 0.81
98 N Westview --- Craig Grabenhorst |  |  | 305 N Deerlane --
465 N Fawn DR -- Martin Klinger |  |  | 655 N Wayside -- Community Center
2345 N Silverside -- John Balden
Page 6 of 8

## Well
Panther Creek Water District Well Report
Month: Year: |  | SEP | 2023
Date | Beginning Reading | Ending Reading | Gallons Produced
1 |  |  | 0
2 |  |  | 0
3 |  |  | 0
4 |  |  | 0
5 |  |  | 0
6 |  |  | 0
7 |  |  | 0
8 |  |  | 0
9 |  |  | 0
10 |  |  | 0
11 |  |  | 0
12 |  |  | 0
13 |  |  | 0
14 |  |  | 0
15 |  |  | 0
16 |  |  | 0
17 |  |  | 0
18 |  |  | 0
19 |  |  | 0
20 |  |  | 0
21 |  |  | 0
22 |  |  | 0
23 |  |  | 0
24 |  |  | 0
25 |  |  | 0
26 |  |  | 0
27 |  |  | 0
28 |  |  | 0
29 |  |  | 0
30 |  |  | 0
31 |  |  | 0
panther Creek Water District Well Report |  |  | 0
Page 7 of 8

## Gen
Generator Log |  |  |  | SEP
2023
Date | Start Hours | Shut Off Hours | Hours | Comments
Ran
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
Page 8 of 8