## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-08-01
System Name: | Panther Creek |  |  | ID#: 4100603 |  |  | WTP : TP - | Panther creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Ward Allen Blanchard
[5 empty] | SIGNATURE: |  |  | 2025-09-01
[5 empty] | PHONE #: ( 541-992-3214 ) |  |  | CERT #: 419241
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Panther Creek
System Name: | Panther creek |  | ID#: 41 | 00603 | Month/Year: |  | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.85 | 82.6 | 70.21 | 12 | 7.95 | 46.3998 | YES | 74.5
2 | 0.8 | 82.6 | 66.08 | 12 | 7.66 | 41.6674 | YES | 72.3
3 | 0.51 | 82.6 | 42.126 | 12 | 7.68 | 40.6168 | YES | 71.4
4 | 1.07 | 82.6 | 88.382 | 12 | 7.67 | 43.1031 | YES | 72.3
5 | 0.86 | 82.6 | 71.036 | 12 | 7.61 | 41.2228 | YES | 71.4
6 | 1.04 | 82.6 | 85.904 | 12 | 7.72 | 43.7181 | YES | 68.7
7 | 1.03 | 82.6 | 85.078 | 12 | 7.75 | 44.1316 | YES | 72.1
8 | 1 | 82.6 | 82.6 | 12 | 7.77 | 44.2927 | YES | 77.4
9 | 0.75 | 82.6 | 61.95 | 12 | 7.55 | 39.8761 | YES | 80.4
10 | 0.66 | 82.6 | 54.516 | 12 | 7.66 | 41.0181 | YES | 70.4
11 | 1.13 | 82.6 | 93.338 | 12 | 7.52 | 41.1762 | YES | 73.5
12 | 1.19 | 82.6 | 98.294 | 12 | 7.44 | 40.3139 | YES | 66.2
13 | 1.35 | 82.6 | 111.51 | 12 | 7.4 | 40.4745 | YES | 68.3
14 | 1.27 | 82.6 | 104.902 | 12 | 7.47 | 41.1042 | YES | 65.2
15 | 1.22 | 82.6 | 100.772 | 12 | 7.48 | 41.0173 | YES | 63.7
16 | 1.43 | 82.6 | 118.118 | 12 | 7.54 | 42.8872 | YES | 67.4
17 | 0.99 | 82.6 | 81.774 | 12 | 7.43 | 39.2866 | YES | 70.5
18 | 1.02 | 82.6 | 84.252 | 12 | 7.39 | 38.8751 | YES | 72.4
19 | 1.33 | 82.6 | 109.858 | 12 | 7.39 | 40.2437 | YES | 81.2
20 | 1.44 | 82.6 | 118.944 | 12 | 7.34 | 40.039 | YES | 79.3
21 | 1.22 | 82.6 | 100.772 | 12 | 7.37 | 39.4767 | YES | 75.2
22 | 1.08 | 82.6 | 89.208 | 12 | 7.41 | 39.4084 | YES | 74.7
23 | 0.93 | 82.6 | 76.818 | 12 | 7.44 | 39.1603 | YES | 78.6
24 | 1.35 | 82.6 | 111.51 | 12 | 7.53 | 42.3541 | YES | 70.7
25 | 0.65 | 82.6 | 53.69 | 12 | 7.5 | 38.7555 | YES | 77.9
26 | 0.56 | 82.6 | 46.256 | 12 | 7.3 | 35.8146 | YES | 70.2
27 | 1.81 | 82.6 | 149.506 | 12 | 8.27 | 58.0768 | YES | 67.3
28 | 1.42 | 82.6 | 117.292 | 12 | 7.58 | 43.4442 | YES | 63.8
29 | 1.19 | 82.6 | 98.294 | 12 | 7.38 | 39.4817 | YES | 75.3
30 | 1.97 | 82.6 | 162.722 | 12 | 7.47 | 44.4754 | YES | 71.3
31 | 0.91 | 82.6 | 75.166 | 12 | 7.61 | 41.4546 | YES | 73.2
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2