## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-10-01
System Name: | Panther Creek |  |  | ID#: 4100603 |  |  | WTP : TP - | Panther creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Ward Allen Blanchard
SIGNATURE:
[5 empty] | PHONE #: ( 541-992-3214 ) |  |  | CERT #: 419241
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Panther Creek
System Name: | Panther creek |  | ID#: 41 | 00603 | Month/Year: | 2025-10-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.32 | 71.41 | 94.2612 | 12 | 7.47 | 41.3354 | YES | 78.4
2 | 1.48 | 71.41 | 105.6868 | 12.1 | 7.38 | 40.5169 | YES | 74.3
3 | 1.77 | 71.41 | 126.3957 | 12 | 7.47 | 43.4819 | YES | 77.8
4 | 1.03 | 71.41 | 73.5523 | 12.1 | 7.49 | 40.0318 | YES | 77.4
5 | 1.01 | 71.41 | 72.1241 | 12 | 7.52 | 40.6263 | YES | 74.2
6 | 0.91 | 71.41 | 64.9831 | 12.1 | 7.5 | 39.6364 | YES | 80.4
7 | 0.98 | 71.41 | 69.9818 | 12 | 7.49 | 40.0695 | YES | 69.3
8 | 1.77 | 71.41 | 126.3957 | 12.1 | 7.53 | 44.1164 | YES | 72.4
9 | 1.72 | 71.41 | 122.8252 | 12.1 | 7.62 | 45.28 | YES | 78.4
10 | 1.58 | 71.41 | 112.8278 | 12.1 | 7.56 | 43.6376 | YES | 76.3
11 | 1.28 | 71.41 | 91.4048 | 12 | 7.6 | 43.065 | YES | 75.8
12 | 1.11 | 71.41 | 79.2651 | 12.1 | 7.47 | 40.1114 | YES | 72.3
13 | 1.19 | 71.41 | 84.9779 | 12 | 7.65 | 43.3847 | YES | 78.4
14 | 1.34 | 71.41 | 95.6894 | 12.1 | 7.64 | 43.6818 | YES | 74.2
15 | 1.23 | 71.41 | 87.8343 | 12 | 7.62 | 43.1244 | YES | 73.2
16 | 1.63 | 71.41 | 116.3983 | 12.1 | 7.67 | 45.6179 | YES | 75.2
17 | 0.81 | 71.41 | 57.8421 | 12 | 7.63 | 41.2794 | YES | 76.2
18 | 1.58 | 71.41 | 112.8278 | 12.1 | 7.67 | 45.3601 | YES | 73.6
19 | 1 | 71.41 | 71.41 | 12 | 7.59 | 41.584 | YES | 71.3
20 | 1.2 | 71.41 | 85.692 | 12.1 | 7.67 | 43.4525 | YES | 74.3
21 | 1.02 | 71.41 | 72.8382 | 12 | 7.69 | 43.1626 | YES | 72.4
22 | 1.42 | 71.41 | 101.4022 | 12.1 | 7.67 | 44.5458 | YES | 82.3
23 | 1.54 | 71.41 | 109.9714 | 12 | 7.68 | 45.6154 | YES | 73.3
24 | 1.35 | 71.41 | 96.4035 | 12.1 | 7.69 | 44.5067 | YES | 77.2
25 | 1.29 | 71.41 | 92.1189 | 12 | 7.68 | 44.3424 | YES | 87.2
26 | 1.14 | 71.41 | 81.4074 | 12.1 | 7.87 | 46.3084 | YES | 77.3
27 | 1.1 | 71.41 | 78.551 | 12 | 7.75 | 44.4822 | YES | 76.2
28 | 1.18 | 71.41 | 84.2638 | 12.1 | 7.7 | 43.8137 | YES | 79.3
29 | 1.84 | 71.41 | 131.3944 | 12 | 7.69 | 47.364 | YES | 75.2
30 | 0.98 | 71.41 | 69.9818 | 12.1 | 7.76 | 43.7481 | YES | 72.2
31 | 0.99 | 71.41 | 70.6959 | 12 | 7.61 | 41.8287 | YES | 80.7
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2