## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-11-25
System Name: | Panther Creek |  |  | ID#: 4100603 |  |  | WTP : TP - | Panther creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Ward Allen Blanchard
SIGNATURE:
[5 empty] | PHONE #: ( 541-992-3214 ) |  |  | CERT #: 419241
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Panther Creek
System Name: | Panther creek |  | ID#: 41 | 00603 | Month/Year: | 2025-11-30 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.85 | 71.41 | 60.6985 | 12 | 7.43 | 38.6786 | YES | 75.3
2 | 0.87 | 71.41 | 62.1267 | 12.1 | 7.7 | 42.3095 | YES | 74.5
3 | 0.8 | 71.41 | 57.128 | 12 | 7.85 | 44.5386 | YES | 74.3
4 | 1.4 | 71.41 | 99.974 | 12.1 | 7.53 | 42.3141 | YES | 76.4
5 | 1.66 | 71.41 | 118.5406 | 12 | 7.89 | 49.816 | YES | 75.2
6 | 1.64 | 71.41 | 117.1124 | 12.1 | 7.85 | 48.6747 | YES | 76.2
7 | 1.21 | 71.41 | 86.4061 | 12 | 7.75 | 45.0394 | YES | 75.9
8 | 1.62 | 71.41 | 115.6842 | 12.1 | 7.98 | 50.8629 | YES | 74.3
9 | 2.06 | 71.41 | 147.1046 | 12 | 7.72 | 49.0867 | YES | 72.4
10 | 1.57 | 71.41 | 112.1137 | 12.1 | 7.69 | 45.6295 | YES | 78.43
11 | 1.37 | 71.41 | 97.8317 | 12 | 7.79 | 46.5164 | YES | 72.3
12 | 1.41 | 71.41 | 100.6881 | 12.1 | 7.6 | 43.4141 | YES | 81.2
13 | 1.89 | 71.41 | 134.9649 | 12 | 7.61 | 46.3047 | YES | 78.4
14 | 2.06 | 71.41 | 147.1046 | 12.1 | 7.69 | 48.244 | YES | 76.3
15 | 1.57 | 71.41 | 112.1137 | 12 | 7.73 | 46.5866 | YES | 77.6
16 | 1.28 | 71.41 | 91.4048 | 12.1 | 7.67 | 43.8466 | YES | 78.4
17 | 1.08 | 71.41 | 77.1228 | 12 | 7.64 | 42.7002 | YES | 73.5
18 | 1.1 | 71.41 | 78.551 | 12.1 | 7.67 | 42.9653 | YES | 64.3
19 | 1.4 | 71.41 | 99.974 | 12 | 7.7 | 45.2152 | YES | 73.4
20 | 1.36 | 71.41 | 97.1176 | 12.1 | 7.7 | 44.7143 | YES | 78.5
21 | 0.9 | 71.41 | 64.269 | 12 | 7.79 | 44.1041 | YES | 75.8
22 | 0.75 | 71.41 | 53.5575 | 12.1 | 7.77 | 42.778 | YES | 72.6
23 | 1.6 | 71.41 | 114.256 | 12 | 7.7 | 46.2525 | YES | 74.6
24 | 1.83 | 71.41 | 130.6803 | 12.1 | 7.75 | 48.0065 | YES | 71.4
25 | 1.51 | 71.41 | 107.8291 | 12 | 7.84 | 48.1078 | YES | 70.5
26 | 1.21 | 71.41 | 86.4061 | 12.1 | 7.76 | 44.9005 | YES | 78.2
27 | 1.38 | 71.41 | 98.5458 | 12 | 7.74 | 45.7539 | YES | 67.3
28 | 1.44 | 71.41 | 102.8304 | 12.1 | 7.73 | 45.601 | YES | 74.8
29 | 0.86 | 71.41 | 61.4126 | 12 | 7.71 | 42.6898 | YES | 80.3
30 | 0.97 | 71.41 | 69.2677 | 12.1 | 7.68 | 42.4896 | YES | 76.3
31 |  | 71.41
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2