## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2025-12-01
System Name: | Panther Creek |  |  | ID#: 4100603 |  |  | WTP : TP - | Panther creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Ward Allen Blanchard
SIGNATURE:
[5 empty] | PHONE #: ( 541-992-3214 ) |  |  | CERT #: 419241
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Panther Creek
System Name: | Panther creek |  | ID#: 41 | 00603 | Month/Year: | 2025-12-01 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.41 | 71.41 | 100.6881 | 12.1 | 7.72 | 45.2861 | YES | 78.2
2 | 1.36 | 71.41 | 97.1176 | 12 | 7.67 | 44.5378 | YES | 74.3
3 | 1.44 | 71.41 | 102.8304 | 12.1 | 7.73 | 45.601 | YES | 81.9
4 | 1.41 | 71.41 | 100.6881 | 12 | 7.67 | 44.7904 | YES | 78.4
5 | 0.9 | 71.41 | 64.269 | 12.1 | 7.72 | 42.751 | YES | 79.3
6 | 1.3 | 71.41 | 92.833 | 12 | 7.7 | 44.7062 | YES | 81.2
7 | 1.1 | 71.41 | 78.551 | 12.1 | 7.77 | 44.5015 | YES | 78.2
8 | 1 | 71.41 | 71.41 | 12 | 7.74 | 43.828 | YES | 72.6
9 | 0.9 | 71.41 | 64.269 | 12.1 | 7.71 | 42.6015 | YES | 73.2
10 | 1.2 | 71.41 | 85.692 | 12 | 7.67 | 43.7398 | YES | 70.4
11 | 1.3 | 71.41 | 92.833 | 12.1 | 7.7 | 44.4118 | YES | 73.2
12 | 1.2 | 71.41 | 85.692 | 12 | 7.66 | 43.5864 | YES | 74.3
13 | 1.3 | 71.41 | 92.833 | 12.1 | 7.67 | 43.9457 | YES | 75.7
14 | 1.49 | 71.41 | 106.4009 | 12 | 7.65 | 44.8806 | YES | 78.4
15 | 1.1 | 71.41 | 78.551 | 12.1 | 7.64 | 42.516 | YES | 78.3
16 | 1.41 | 71.41 | 100.6881 | 12 | 7.61 | 43.8549 | YES | 73.2
17 | 1.33 | 71.41 | 94.9753 | 12.1 | 7.6 | 43.0243 | YES | 77.5
18 | 1.47 | 71.41 | 104.9727 | 12 | 7.64 | 44.6217 | YES | 81.3
19 | 1.75 | 71.41 | 124.9675 | 12.1 | 7.56 | 44.4838 | YES | 76.3
20 | 1.4 | 71.41 | 99.974 | 12 | 7.58 | 43.3463 | YES | 74.5
21 | 1.37 | 71.41 | 97.8317 | 12.1 | 7.66 | 44.1392 | YES | 75.5
22 | 1.81 | 71.41 | 129.2521 | 12 | 7.68 | 47.0358 | YES | 76.2
23 | 1.61 | 71.41 | 114.9701 | 12.1 | 7.74 | 46.654 | YES | 77.3
24 | 0.75 | 71.41 | 53.5575 | 12 | 7.65 | 41.2898 | YES | 75.8
25 | 1.07 | 71.41 | 76.4087 | 12.1 | 7.6 | 41.784 | YES | 76.2
26 | 0.86 | 71.41 | 61.4126 | 12 | 7.6 | 41.0792 | YES | 79.3
27 | 1.06 | 71.41 | 75.6946 | 12.1 | 7.6 | 41.7371 | YES | 71.4
28 | 0.82 | 71.41 | 58.5562 | 12 | 7.66 | 41.7611 | YES | 80.6
29 | 1.1 | 71.41 | 78.551 | 12.1 | 7.64 | 42.516 | YES | 78.2
30 | 1.16 | 71.41 | 82.8356 | 12 | 7.66 | 43.3902 | YES | 71.8
31 | 1.29 | 71.41 | 92.1189 | 12.1 | 7.7 | 44.3616 | YES | 77
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2