## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2026-01-26
System Name: | Panther Creek |  |  | ID#: 4100603 |  |  | WTP : TP - | Panther creek
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes / No | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes / No | Yes / No |  | Yes / No
Notes: |  |  |  |  | PRINTED NAME: Ward Allen Blanchard
SIGNATURE:
[5 empty] | PHONE #: ( 541-992-3214 ) |  |  | CERT #: 419241
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | Panther Creek
System Name: | Panther creek |  | ID#: 41 | 00603 | Month/Year: | 2026-01-26 | Disinfection Giardia Log Inactiv: | 1
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.39 | 71.41 | 99.2599 | 12 | 7.58 | 43.2975 | YES | 78.3
2 | 0.99 | 71.41 | 70.6959 | 12.1 | 7.64 | 41.9933 | YES | 71.8
3 | 1.17 | 71.41 | 83.5497 | 12 | 7.65 | 43.2869 | YES | 79.7
4 | 0.65 | 71.41 | 46.4165 | 12.1 | 7.6 | 39.8637 | YES | 78.3
5 | 1.25 | 71.41 | 89.2625 | 12 | 7.63 | 43.3737 | YES | 70.2
6 | 1.57 | 71.41 | 112.1137 | 12.1 | 7.64 | 44.8322 | YES | 73.4
7 | 1.37 | 71.41 | 97.8317 | 12 | 7.63 | 43.9652 | YES | 87.6
8 | 1.14 | 71.41 | 81.4074 | 12.1 | 7.65 | 42.8578 | YES | 78.2
9 | 0.9 | 71.41 | 64.269 | 12 | 7.66 | 42.1382 | YES | 74.6
10 | 1.1 | 71.41 | 78.551 | 12.1 | 7.7 | 43.4199 | YES | 63.4
11 | 0.74 | 71.41 | 52.8434 | 12 | 7.65 | 41.2435 | YES | 78.4
12 | 1.08 | 71.41 | 77.1228 | 12.1 | 7.68 | 43.0192 | YES | 74.7
13 | 1.19 | 71.41 | 84.9779 | 12 | 7.65 | 43.3847 | YES | 75.1
14 | 1.13 | 71.41 | 80.6933 | 12.1 | 7.64 | 42.6598 | YES | 78.4
15 | 1.54 | 71.41 | 109.9714 | 12 | 7.7 | 45.9386 | YES | 75.2
16 | 1.32 | 71.41 | 94.2612 | 12.1 | 7.7 | 44.5124 | YES | 76.3
17 | 1.22 | 71.41 | 87.1202 | 12 | 7.65 | 43.5318 | YES | 71.8
18 | 0.82 | 71.41 | 58.5562 | 12.1 | 7.64 | 41.1995 | YES | 70.4
19 | 1.09 | 71.41 | 77.8369 | 12 | 7.69 | 43.5047 | YES | 74.6
20 | 1.26 | 71.41 | 89.9766 | 12.1 | 7.67 | 43.7477 | YES | 77.9
21 | 1.26 | 71.41 | 89.9766 | 12 | 7.37 | 39.6534 | YES | 76.2
22 | 1.25 | 71.41 | 89.2625 | 12.1 | 7.58 | 42.3407 | YES | 77.2
23 | 1.08 | 71.41 | 77.1228 | 12 | 7.59 | 41.9593 | YES | 74.7
24 | 0.95 | 71.41 | 67.8395 | 12.1 | 7.63 | 41.6591 | YES | 71.6
25 | 1 | 71.41 | 71.41 | 12 | 7.65 | 42.4659 | YES | 74.7
26 | 1.58 | 71.41 | 112.8278 | 12.1 | 7.46 | 42.1344 | YES | 78.4
27 | 1.15 | 71.41 | 82.1215 | 12 | 7.52 | 41.2687 | YES | 74.3
28 | 1.5 | 71.41 | 107.115 | 12.1 | 7.53 | 42.793 | YES | 74.5
29 | 1.61 | 71.41 | 114.9701 | 12 | 7.53 | 43.6132 | YES | 75.2
30 | 1.55 | 71.41 | 110.6855 | 12.1 | 7.67 | 45.2062 | YES | 78.2
31 | 1.18 | 71.41 | 84.2638 | 12 | 7.68 | 43.7947 | YES | 71.9
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised November 2022
Return by 10th of following month by email, fax, or mail to: dwp.dmce@oha.oregon.gov; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2