## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2021-01-21
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.07 | 0.04 | OFF | 0.03 | 0.04 | 0.04 | 0.1
2 | 0.03 | 0.03 | OFF | 0.1 | 0.05 | 0.04 | 0.16
3 | 0.21 | 0.14 | OFF | OFF | OFF | OFF | 0.3
4 | OFF | OFF | OFF | OFF | OFF | OFF | 0
5 | OFF | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.11
6 | 0.04 | 0.03 | 0.03 | 0.04 | 0.03 | 0.12 | 0.14
7 | 0.04 | OFF | OFF | 0.06 | 0.04 | 0.03 | 0.08
8 | 0.06 | 0.03 | 0.04 | 0.06 | OFF | OFF | 0.28
9 | 0.04 | OFF | 0.04 | 0.03 | 0.03 | 0.03 | 0.06
10 | 0.05 | 0.03 | 0.04 | 0.03 | 0.03 | 0.03 | 0.06
11 | 0.02 | OFF | OFF | 0.03 | 0.04 | 0.03 | 0.07
12 | OFF | 0.04 | 0.04 | OFF | OFF | OFF | 0.06
13 | OFF | OFF | OFF | 0.12 | 0.04 | 0.04 | 0.2
14 | 0.04 | 0.06 | 0.1 | 0.07 | 0.14 | 0.1 | 0.16
15 | 0.07 | 0.06 | 0.06 | 0.04 | 0.04 | 0.04 | 0.1
16 | 0.04 | 0.04 | OFF | 0.03 | 0.03 | 0.03 | 0.08
17 | 0.03 | OFF | OFF | 0.03 | 0.04 | 0.03 | 0.08
18 | 0.05 | OFF | OFF | 0.04 | 0.03 | 0.03 | 0.07
19 | 0.04 | OFF | OFF | 0.03 | 0.07 | 0.03 | 0.08
20 | 0.04 | OFF | OFF | 0.03 | 0.04 | 0.04 | 0.08
21 | 0.05 | 0.04 | OFF | OFF | 0.03 | 0.03 | 0.08
22 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | OFF | 0.1
23 | OFF | 0.04 | 0.03 | 0.03 | 0.07 | 0.03 | 0.07
24 | 0.02 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.07
25 | OFF | 0.04 | 0.03 | 0.03 | 0.07 | 0.03 | 0.07
26 | 0.05 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.08
27 | 0.05 | 0.03 | 0.03 | 0.03 | 0.04 | 0.03 | 0.08
28 | OFF | OFF | OFF | 0.08 | 0.04 | 0.03 | 0.08
29 | 0.04 | 0.05 | 0.03 | OFF | 0.03 | 0.04 | 0.08
30 | 0.05 | 0.03 | OFF | OFF | 0.03 | 0.03 | 0.08
31 | 0.06 | 0.04 | 0.03 | OFF | 0.04 | 0.04 | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2021-02-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2021-01-21 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.24 | 146.3415 | 181.4634 | 7.7 | 7 | 26 | Y | 410
2 / | 12:00 | 1.27 | 146.3415 | 185.8537 | 7.8 | 7.1 | 31 | Y | 410
3 / | 9:00 | 1.08 | 146.3415 | 158.0488 | 9.4 | 7 | 25 | Y | 410
4 / | 11:00 | 0.84 | 0 | 0 | 9.5 | 7 | 0 | Y | 0
5 / | 9:00 | 0.75 | 146.3415 | 109.7561 | 9.6 | 6.9 | 24 | Y | 410
6 / | 8:00 | 1.26 | 146.3415 | 184.3902 | 9 | 6.9 | 26 | Y | 410
7 / | 9:00 | 1.15 | 146.3415 | 168.2927 | 9.4 | 6.9 | 25 | Y | 410
8 / | 9:00 | 1.26 | 146.3415 | 184.3902 | 9 | 7 | 26 | Y | 410
9 / | 9:00 | 1.05 | 146.3415 | 153.6585 | 9.1 | 7 | 25 | Y | 410
10/ | 9:00 | 1.32 | 146.3415 | 193.1707 | 8.7 | 6.8 | 26 | Y | 410
11/ | 9:00 | 1.23 | 146.3415 | 180 | 9.2 | 6.9 | 26 | Y | 410
12/ | 8:00 | 1.24 | 146.3415 | 181.4634 | 9.3 | 6.9 | 26 | Y | 410
13/ | 6:00 | 1.07 | 146.3415 | 156.5854 | 9.5 | 6.9 | 25 | Y | 410
14/ | 10:00 | 1.24 | 146.3415 | 181.4634 | 9.4 | 6.9 | 26 | Y | 410
15/ | 10:00 | 1.1 | 146.3415 | 160.9756 | 9.3 | 6.9 | 25 | Y | 410
16/ | 8:00 | 1.23 | 146.3415 | 180 | 9.5 | 7.1 | 31 | Y | 410
17/ | 5:00 | 1.24 | 146.3415 | 181.4634 | 9.7 | 6.9 | 26 | Y | 410
18/ | 9:00 | 1.11 | 146.3415 | 162.439 | 9.7 | 6.9 | 25 | Y | 410
19/ | 9:00 | 1.28 | 146.3415 | 187.3171 | 9.1 | 7 | 26 | Y | 410
20/ | 1:00 | 1.26 | 146.3415 | 184.3902 | 8.7 | 7 | 26 | Y | 410
21/ | 9:00 | 1.31 | 146.3415 | 191.7073 | 7.9 | 7 | 26 | Y | 410
22/ | 9:00 | 1.26 | 146.3415 | 184.3902 | 8.2 | 7 | 26 | Y | 410
23/ | 9:00 | 1.29 | 146.3415 | 188.7805 | 7.2 | 7.1 | 31 | Y | 410
24/ | 8:00 | 1.18 | 146.3415 | 172.6829 | 7.9 | 7 | 25 | Y | 410
25/ | 9:00 | 1.25 | 146.3415 | 182.9268 | 6.8 | 7 | 26 | Y | 410
26/ | 9:00 | 1.19 | 146.3415 | 174.1463 | 7.3 | 7 | 25 | Y | 410
27/ | 9:00 | 1.22 | 146.3415 | 178.5366 | 5.7 | 7 | 26 | Y | 410
28/ | 9:00 | 1.09 | 146.3415 | 159.5122 | 8.1 | 7.1 | 31 | Y | 410
29/ | 9:00 | 1.23 | 146.3415 | 180 | 8.3 | 7.1 | 31 | Y | 410
30/ | 9:00 | 1.26 | 146.3415 | 184.3902 | 7.6 | 7.1 | 31 | Y | 410
31/ | 9:00 | 1.26 | 146.3415 | 184.3902 | 7.9 | 7.1 | 31 | Y | 410
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2