## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2021-03-21
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.03 | 0.03 | 0.03 | OFF | 0.03 | 0.03 | 0.07
2 | 0.05 | 0.03 | OFF | 0.03 | 0.03 | 0.03 | 0.1
3 | 0.05 | OFF | OFF | 0.04 | 0.03 | 0.05 | 0.09
4 | 0.06 | 0.03 | OFF | 0.03 | 0.05 | 0.04 | 0.1
5 | 0.05 | 0.04 | OFF | OFF | 0.03 | 0.03 | 0.1
6 | 0.05 | 0.03 | OFF | 0.02 | 0.03 | 0.06 | 0.06
7 | 0.05 | OFF | OFF | 0.03 | 0.03 | 0.02 | 0.06
8 | 0.04 | 0.04 | 0.04 | OFF | OFF | 0.03 | 0.1
9 | 0.04 | 0.04 | 0.03 | OFF | 0.03 | 0.04 | 0.1
10 | 0.05 | 0.03 | 0.04 | 0.04 | OFF | OFF | 0.09
11 | 0.06 | 0.06 | 0.04 | 0.03 | OFF | 0.06 | 0.12
12 | 0.08 | 0.08 | 0.05 | 0.05 | 0.03 | 0.03 | 0.1
13 | 0.04 | OFF | 0.03 | 0.03 | 0.03 | 0.03 | 0.07
14 | 0.04 | 0.03 | OFF | OFF | 0.04 | 0.04 | 0.07
15 | 0.06 | 0.03 | 0.06 | 0.03 | 0.03 | 0.04 | 0.09
16 | 0.05 | OFF | OFF | 0.03 | 0.04 | 0.04 | 0.1
17 | 0.05 | 0.04 | 0.04 | OFF | OFF | 0.04 | 0.1
18 | 0.05 | 0.03 | 0.03 | 0.04 | 0.03 | 0.04 | 0.1
19 | 0.05 | OFF | OFF | 0.04 | 0.03 | 0.04 | 0.1
20 | 0.06 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.08
21 | 0.04 | OFF | OFF | 0.04 | 0.03 | 0.03 | 0.07
22 | 0.04 | 0.03 | 0.03 | OFF | 0.04 | 0.04 | 0.08
23 | 0.05 | 0.04 | 0.04 | 0.04 | OFF | OFF | 0.12
24 | 0.04 | 0.04 | 0.04 | OFF | OFF | 0.06 | 0.08
25 | 0.04 | 0.03 | 0.04 | 0.04 | OFF | OFF | 0.08
26 | 0.04 | 0.04 | 0.04 | 0.04 | OFF | 0.04 | 0.09
27 | 0.04 | 0.03 | OFF | OFF | 0.04 | 0.03 | 0.06
28 | 0.05 | 0.04 | OFF | 0.04 | 0.03 | 0.03 | 0.06
29 | 0.08 | 0.04 | OFF | 0.04 | 0.04 | 0.04 | 0.09
30 | 0.03 | 0.04 | OFF | 0.04 | 0.04 | 0.03 | 0.09
31 | 0.04 | 0.05 | 0.05 | OFF | OFF | 0.03 | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2021-04-04
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2021-03-21 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.45 | 146.3415 | 212.1951 | 8.1 | 7 | 26 | Y | 410
2 / | 9:00 | 1.23 | 146.3415 | 180 | 8.5 | 7 | 26 | Y | 410
3 / | 9:00 | 1.17 | 146.3415 | 171.2195 | 9.2 | 7 | 25 | Y | 410
4 / | 10:00 | 1.26 | 146.3415 | 184.3902 | 9.3 | 7 | 26 | Y | 410
5 / | 9:00 | 1.16 | 146.3415 | 169.7561 | 8.5 | 7 | 25 | Y | 410
6 / | 9:00 | 1.14 | 146.3415 | 166.8293 | 8.9 | 7 | 25 | Y | 410
7 / | 9:00 | 1.19 | 146.3415 | 174.1463 | 8.8 | 7.1 | 31 | Y | 410
8 / | 9:00 | 1.18 | 146.3415 | 172.6829 | 7.7 | 7 | 25 | Y | 410
9 / | 9:00 | 1.26 | 146.3415 | 184.3902 | 7.5 | 7 | 26 | Y | 410
10/ | 9:00 | 1.18 | 146.3415 | 172.6829 | 7.7 | 7 | 25 | Y | 410
11/ | 9:00 | 1.18 | 146.3415 | 172.6829 | 7.3 | 7 | 25 | Y | 410
12/ | 9:00 | 1.18 | 146.3415 | 172.6829 | 7.3 | 7 | 25 | Y | 410
13/ | 9:00 | 1.06 | 146.3415 | 155.122 | 8.1 | 7.1 | 31 | Y | 410
14/ | 9:00 | 1.15 | 146.3415 | 168.2927 | 8.4 | 7.1 | 31 | Y | 410
15/ | 9:00 | 1.04 | 146.3415 | 152.1951 | 7.9 | 7.1 | 31 | Y | 410
16/ | 9:00 | 1.04 | 146.3415 | 152.1951 | 7.8 | 7.1 | 31 | Y | 410
17/ | 9:00 | 1.15 | 146.3415 | 168.2927 | 6.6 | 7.1 | 31 | Y | 410
18/ | 9:00 | 1.15 | 146.3415 | 168.2927 | 7.5 | 7.1 | 31 | Y | 410
19/ | 9:00 | 1.1 | 146.3415 | 160.9756 | 8.4 | 7.1 | 31 | Y | 410
20/ | 9:00 | 1.05 | 146.3415 | 153.6585 | 8.2 | 7.1 | 31 | Y | 410
21/ | 8:00 | 0.99 | 146.3415 | 144.878 | 8.7 | 7.5 | 30 | Y | 410
22/ | 7:00 | 1.12 | 146.3415 | 163.9024 | 8.4 | 7 | 25 | Y | 410
23/ | 9:00 | 1.01 | 146.3415 | 147.8049 | 8.1 | 7.1 | 31 | Y | 410
24/ | 9:00 | 1.18 | 146.3415 | 172.6829 | 8.2 | 7 | 25 | Y | 410
25/ | 9:00 | 1.17 | 146.3415 | 171.2195 | 8.4 | 7 | 25 | Y | 410
26/ | 9:00 | 0.99 | 146.3415 | 144.878 | 7.9 | 7 | 25 | Y | 410
27/ | 9:00 | 1.17 | 146.3415 | 171.2195 | 7.8 | 7.1 | 31 | Y | 410
28/ | 8:00 | 1.16 | 146.3415 | 169.7561 | 9.1 | 7 | 25 | Y | 410
29/ | 9:00 | 1.13 | 146.3415 | 165.3659 | 8.9 | 7 | 25 | Y | 410
30/ | 9:00 | 1.15 | 146.3415 | 168.2927 | 8.6 | 7 | 25 | Y | 410
31/ | 9:00 | 1.19 | 146.3415 | 174.1463 | 8.1 | 7 | 25 | Y | 410
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2