## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2021-08-21
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.1 | OFF | 0.16 | 0.1 | 0.11 | 0.11 | 0.16
2 | 0.11 | OFF | 0.09 | 0.1 | 0.11 | 0.11 | 0.15
3 | 0.1 | 0.1 | 0.12 | 0.18 | 0.11 | 0.13 | 0.18
4 | 0.1 | 0.11 | 0.09 | 0.1 | 0.1 | 0.12 | 0.14
5 | 0.11 | 0.1 | 0.1 | 0.09 | 0.12 | OFF | 0.15
6 | 0.09 | OFF | 0.1 | 0.09 | 0.1 | OFF | 0.14
7 | 0.15 | OFF | 0.09 | 0.1 | 0.1 | OFF | 0.15
8 | 0.11 | OFF | 0.11 | 0.09 | OFF | 0.11 | 0.16
9 | 0.1 | OFF | 0.18 | 0.09 | OFF | 0.1 | 0.18
10 | OFF | 0.09 | 0.09 | 0.09 | OFF | 0.16 | 0.16
11 | 0.13 | 0.1 | 0.12 | 0.1 | 0.14 | OFF | 0.14
12 | 0.1 | OFF | 0.17 | OFF | 0.12 | 0.14 | 0.17
13 | 0.14 | OFF | 0.12 | 0.1 | 0.11 | 0.18 | 0.18
14 | 0.11 | OFF | 0.09 | 0.1 | 0.12 | OFF | 0.15
15 | 0.09 | OFF | 0.11 | 0.1 | 0.1 | 0.11 | 0.15
16 | 0.11 | OFF | 0.1 | 0.1 | OFF | 0.12 | 0.16
17 | 0.12 | OFF | 0.09 | 0.1 | 0.1 | OFF | 0.13
18 | OFF | 0.09 | 0.1 | 0.09 | OFF | OFF | 0.19
19 | 0.08 | OFF | 0.12 | 0.09 | OFF | 0.1 | 0.13
20 | 0.11 | OFF | 0.09 | 0.09 | 0.1 | OFF | 0.12
21 | 0.09 | OFF | 0.07 | 0.08 | OFF | OFF | 0.12
22 | 0.1 | OFF | 0.08 | OFF | OFF | 0.08 | 0.12
23 | OFF | OFF | 0.08 | 0.16 | OFF | 0.07 | 0.16
24 | OFF | OFF | 0.09 | OFF | OFF | 0.08 | 0.15
25 | 0.08 | OFF | 0.08 | 0.08 | 0.13 | OFF | 0.13
26 | 0.09 | 0.1 | 0.1 | 0.1 | 0.12 | OFF | 0.17
27 | 0.1 | 0.1 | 0.11 | 0.1 | 0.09 | 0.14 | 0.17
28 | 0.1 | 0.09 | 0.08 | 0.08 | 0.09 | OFF | 0.14
29 | 0.09 | 0.08 | 0.09 | 0.08 | 0.08 | 0.1 | 0.15
30 | 0.11 | OFF | 0.09 | 0.18 | 0.09 | 0.09 | 0.18
31 | 0.09 | 0.09 | 0.08 | 0.07 | 0.09 | 0.08 | 0.17
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2021-09-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2021-08-21 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.19 | 69.4444 | 82.6389 | 22 | 7.1 | 23 | Y | 864
2 / | 8:00 | 1.21 | 69.4444 | 84.0278 | 22.4 | 7.1 | 23 | Y | 864
3 / | 9:00 | 1.2 | 69.4444 | 83.3333 | 22.2 | 7.1 | 23 | Y | 864
4 / | 9:00 | 1.12 | 69.4444 | 77.7778 | 20.9 | 7.1 | 23 | Y | 864
5 / | 9:00 | 1.1 | 69.4444 | 76.3889 | 21.3 | 7.1 | 23 | Y | 864
6 / | 9:00 | 1.24 | 69.4444 | 86.1111 | 20 | 7.1 | 23 | Y | 864
7 / | 8:00 | 1.13 | 69.4444 | 78.4722 | 20.3 | 7.1 | 23 | Y | 864
8 / | 8:00 | 1.12 | 69.4444 | 77.7778 | 19.8 | 7.1 | 31 | Y | 864
9 / | 9:00 | 1.12 | 69.4444 | 77.7778 | 19.5 | 7.1 | 31 | Y | 864
10/ | 9:00 | 1.16 | 69.4444 | 80.5556 | 19.8 | 7.1 | 31 | Y | 864
11/ | 8:00 | 1.09 | 69.4444 | 75.6944 | 21.2 | 7.1 | 23 | Y | 864
12/ | 8:00 | 0.99 | 69.4444 | 68.75 | 23.1 | 7.1 | 22 | Y | 864
13/ | 8:00 | 1.27 | 69.4444 | 88.1944 | 22.3 | 7.1 | 23 | Y | 864
14/ | 8:00 | 1.22 | 69.4444 | 84.7222 | 22.1 | 7.1 | 23 | Y | 864
15/ | 8:00 | 0.99 | 69.4444 | 68.75 | 21.9 | 7.1 | 22 | Y | 864
16/ | 8:00 | 1.13 | 69.4444 | 78.4722 | 20.6 | 7.1 | 23 | Y | 864
17/ | 9:00 | 1.09 | 69.4444 | 75.6944 | 21 | 7.1 | 23 | Y | 864
18/ | 9:00 | 1.2 | 69.4444 | 83.3333 | 18 | 7.1 | 31 | Y | 864
19/ | 10:00 | 1.24 | 69.4444 | 86.1111 | 17.9 | 7.1 | 31 | Y | 864
20/ | 8:00 | 1.25 | 69.4444 | 86.8056 | 19.3 | 7.1 | 31 | Y | 864
21/ | 9:00 | 1.2 | 69.4444 | 83.3333 | 19.6 | 7.1 | 31 | Y | 864
22/ | 11:00 | 1.21 | 69.4444 | 84.0278 | 17.9 | 7.1 | 31 | Y | 864
23/ | 9:00 | 1.3 | 69.4444 | 90.2778 | 17.1 | 7.1 | 31 | Y | 864
24/ | 9:00 | 1.27 | 69.4444 | 88.1944 | 16.8 | 7.1 | 31 | Y | 864
25/ | 9:00 | 1.28 | 84.507 | 108.169 | 17.5 | 7.1 | 31 | Y | 710
26/ | 9:00 | 1.08 | 84.507 | 91.2676 | 17.8 | 7.1 | 31 | Y | 710
27/ | 9:00 | 0.88 | 84.507 | 74.3662 | 18.1 | 7.1 | 30 | Y | 710
28/ | 9:00 | 1.24 | 84.507 | 104.7887 | 17.5 | 7.1 | 31 | Y | 710
29/ | 8:00 | 1.23 | 84.507 | 103.9437 | 17.9 | 7.1 | 31 | Y | 710
30/ | 9:00 | 1.07 | 84.507 | 90.4225 | 17.9 | 7.1 | 31 | Y | 710
31/ | 8:00 | 1.1 | 84.507 | 92.9577 | 17.6 | 7.2 | 31 | Y | 710
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2