## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2021-12-01
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.04 | 0.04 | 0.04 | OFF | 0.06 | 0.05 | 0.11
2 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.12
3 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | OFF | 0.1
4 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.1
5 | OFF | OFF | 0.04 | 0.03 | 0.04 | 0.03 | 0.1
6 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.1
7 | 0.05 | OFF | OFF | 0.05 | 0.13 | 0.07 | 0.24
8 | 0.05 | 0.05 | 0.05 | OFF | OFF | 0.06 | 0.15
9 | 0.05 | 0.05 | 0.04 | 0.04 | 0.06 | 0.04 | 0.16
10 | 0.04 | OFF | OFF | 0.05 | 0.06 | 0.05 | 0.16
11 | 0.04 | 0.04 | OFF | OFF | OFF | OFF | 0.24
12 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | OFF | OFF | OFF | OFF | 0.06 | 0.04 | 0.26
14 | 0.15 | 0.1 | OFF | OFF | 0.04 | 0.08 | 0.16
15 | 0.05 | 0.04 | OFF | 0.03 | 0.04 | 0.04 | 0.1
16 | 0.04 | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.1
17 | 0.04 | 0.1 | OFF | OFF | 0.04 | 0.1 | 0.1
18 | 0.05 | 0.03 | OFF | 0.03 | 0.03 | 0.06 | 0.09
19 | 0.04 | 0.04 | OFF | OFF | 0.08 | 0.07 | 0.3
20 | 0.19 | OFF | OFF | OFF | OFF | 0.07 | 0.3
21 | 0.05 | OFF | OFF | 0.06 | 0.06 | 0.04 | 0.2
22 | 0.12 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.12
23 | 0.04 | OFF | OFF | 0.08 | 0.04 | OFF | 0.1
24 | OFF | OFF | 0.04 | 0.04 | 0.05 | 0.05 | 0.12
25 | OFF | OFF | OFF | 0.03 | 0.04 | 0.04 | 0.1
26 | OFF | OFF | OFF | 0.03 | 0.04 | 0.04 | 0.1
27 | 0.04 | 0.04 | OFF | 0.05 | 0.03 | 0.03 | 0.09
28 | 0.04 | OFF | 0.04 | 0.04 | 0.03 | 0.05 | 0.12
29 | 0.05 | OFF | 0.04 | 0.04 | 0.1 | 0.05 | 0.11
30 | OFF | OFF | OFF | 0.11 | 0.04 | 0.04 | 0.11
31 | 0.05 | 0.1 | OFF | OFF | 0.04 | 0.04 | 0.12
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2022-01-02
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2021-12-01 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.17 | 150 | 175.5 | 10.3 | 7 | 19 | Y | 400
2 / | 9:00 | 0.98 | 150 | 147 | 11 | 7 | 19 | Y | 400
3 / | 9:00 | 1.19 | 150 | 178.5 | 9.5 | 7 | 25 | Y | 400
4 / | 9:00 | 1.21 | 150 | 181.5 | 8.1 | 7 | 26 | Y | 400
5 / | 8:00 | 1.19 | 150 | 178.5 | 7.9 | 7 | 25 | Y | 400
6 / | 9:00 | 1.18 | 150 | 177 | 8.1 | 7.1 | 31 | Y | 400
7 / | 9:00 | 1.03 | 150 | 154.5 | 9.4 | 7.1 | 31 | Y | 400
8 / | 9:00 | 1.15 | 150 | 172.5 | 9.7 | 7.1 | 31 | Y | 400
9 / | 10:00 | 1.1 | 150 | 165 | 8.4 | 7 | 25 | Y | 400
10/ | 9:00 | 1.12 | 150 | 168 | 8.6 | 7 | 25 | Y | 400
11/ | 9:00 | 1.04 | 150 | 156 | 8.3 | 7.1 | 31 | Y | 400
12/ | 9:00 | OFF | 150 | OFF | OFF | OFF | 0 | Y | 400
13/ | 8:00 | 1.1 | 150 | 165 | 8 | 7 | 25 | Y | 400
14/ | 9:00 | 1.11 | 150 | 166.5 | 8.1 | 7 | 25 | Y | 400
15/ | 9:00 | 1.04 | 150 | 156 | 8.2 | 7 | 25 | Y | 400
16/ | 9:00 | 1.17 | 150 | 175.5 | 8.5 | 7 | 25 | Y | 400
17/ | 9:00 | 1.2 | 150 | 180 | 8.9 | 7 | 25 | Y | 400
18/ | 12:00 | 1.21 | 150 | 181.5 | 8.5 | 7.1 | 31 | Y | 400
19/ | 9:00 | 1.12 | 150 | 168 | 9.5 | 7 | 25 | Y | 400
20/ | 1:00 | 0.92 | 150 | 138 | 9 | 7 | 25 | Y | 400
21/ | 11:00 | 1.09 | 150 | 163.5 | 9.2 | 7 | 25 | Y | 400
22/ | 9:00 | 1.16 | 150 | 174 | 9 | 7 | 25 | Y | 400
23/ | 10:00 | 1.17 | 150 | 175.5 | 9.2 | 7 | 25 | Y | 400
24/ | 8:00 | 1 | 150 | 150 | 9.1 | 7 | 25 | Y | 400
25/ | 8:00 | 1.17 | 150 | 175.5 | 9.1 | 7 | 25 | Y | 400
26/ | 9:00 | 1 | 150 | 150 | 9.3 | 7 | 25 | Y | 400
27/ | 3:00 | 1.28 | 150 | 192 | 7.9 | 7 | 25 | Y | 400
28/ | 9:00 | 1.22 | 150 | 183 | 7.1 | 7 | 25 | Y | 400
29/ | 9:00 | 1.27 | 150 | 190.5 | 6.9 | 7 | 25 | Y | 400
30/ | 9:00 | 1.19 | 150 | 178.5 | 8 | 7 | 25 | Y | 400
31/ | 9:00 | 1.1 | 150 | 165 | 6.8 | 7 | 25 | Y | 400
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2