## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2022-08-22
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.06 | 0.07 | 0.07 | 0.06 | 0.08 | 0.08 | 0.14
2 | 0.08 | OFF | 0.08 | 0.1 | 0.08 | 0.08 | 0.14
3 | 0.08 | 0.08 | 0.07 | OFF | 0.08 | OFF | 0.13
4 | 0.08 | 0.13 | 0.08 | 0.07 | 0.08 | 0.08 | 0.15
5 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.13
6 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.07 | 0.12
7 | 0.08 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.12
8 | 0.07 | OFF | 0.08 | 0.07 | 0.07 | 0.07 | 0.14
9 | 0.09 | 0.1 | 0.09 | 0.08 | 0.08 | 0.08 | 0.14
10 | 0.08 | OFF | 0.11 | 0.1 | 0.09 | 0.08 | 0.17
11 | 0.07 | OFF | 0.07 | 0.07 | 0.06 | 0.08 | 0.15
12 | 0.06 | 0.12 | 0.06 | OFF | 0.07 | 0.06 | 0.15
13 | 0.11 | OFF | 0.07 | 0.06 | 0.06 | 0.06 | 0.14
14 | 0.09 | OFF | 0.06 | 0.12 | 0.06 | 0.07 | 0.15
15 | 0.07 | OFF | 0.07 | 0.08 | 0.07 | 0.1 | 0.17
16 | 0.08 | 0.07 | 0.07 | 0.08 | 0.09 | 0.07 | 0.16
17 | 0.09 | OFF | 0.07 | 0.08 | 0.08 | 0.1 | 0.16
18 | 0.09 | 0.07 | 0.08 | 0.07 | 0.08 | 0.09 | 0.15
19 | 0.08 | OFF | 0.09 | 0.08 | 0.08 | 0.1 | 0.16
20 | 0.1 | 0.07 | 0.08 | 0.07 | 0.08 | 0.08 | 0.14
21 | 0.11 | OFF | 0.07 | 0.07 | 0.08 | 0.07 | 0.13
22 | 0.09 | OFF | 0.07 | 0.07 | 0.09 | 0.1 | 0.16
23 | 0.1 | 0.1 | 0.08 | 0.07 | 0.08 | 0.09 | 0.18
24 | 0.09 | 0.08 | 0.07 | 0.08 | 0.09 | OFF | 0.15
25 | 0.09 | 0.1 | 0.08 | 0.15 | 0.09 | 0.08 | 0.16
26 | 0.11 | 0.09 | 0.09 | 0.08 | 0.08 | 0.12 | 0.18
27 | 0.1 | OFF | 0.08 | 0.09 | 0.09 | 0.08 | 0.17
28 | 0.12 | 0.12 | 0.08 | 0.09 | 0.09 | 0.09 | 0.16
29 | 0.14 | 0.1 | 0.1 | 0.08 | 0.08 | 0.09 | 0.14
30 | 0.08 | 0.08 | 0.08 | 0.09 | 0.12 | 0.09 | 0.16
31 | 0.09 | OFF | 0.09 | OFF | OFF | 0.09 | 0.16
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2022-09-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2022-08-22 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.17 | 85.7143 | 100.2857 | 21.2 | 6.9 | 19 | Y | 700
2 / | 9:00 | 1.14 | 85.7143 | 97.7143 | 20.1 | 6.9 | 19 | Y | 700
3 / | 9:00 | 1.15 | 85.7143 | 98.5714 | 20.5 | 7 | 19 | Y | 700
4 / | 10:00 | 1.25 | 85.7143 | 107.1429 | 19.1 | 7 | 26 | Y | 700
5 / | 9:00 | 1.22 | 85.7143 | 104.5714 | 18.8 | 7 | 26 | Y | 700
6 / | 8:00 | 1.21 | 85.7143 | 103.7143 | 19 | 6.9 | 26 | Y | 700
7 / | 8:00 | 1.1 | 85.7143 | 94.2857 | 19.5 | 6.9 | 25 | Y | 700
8 / | 9:00 | 1.12 | 85.7143 | 96 | 19.5 | 6.9 | 25 | Y | 700
9 / | 9:00 | 1.2 | 85.7143 | 102.8571 | 18.7 | 6.9 | 25 | Y | 700
10/ | 9:00 | 1.07 | 85.7143 | 91.7143 | 19.7 | 6.9 | 25 | Y | 700
11/ | 9:00 | 1.02 | 85.7143 | 87.4286 | 19.1 | 6.9 | 25 | Y | 700
12/ | 9:00 | 1.12 | 85.7143 | 96 | 18.5 | 6.9 | 25 | Y | 700
13/ | 8:00 | 1.18 | 85.7143 | 101.1429 | 17.9 | 7 | 25 | Y | 700
14/ | 8:00 | 0.92 | 85.7143 | 78.8571 | 18.5 | 6.9 | 25 | Y | 700
15/ | 9:00 | 1.05 | 85.7143 | 90 | 18.9 | 6.9 | 25 | Y | 700
16/ | 9:00 | 1.12 | 85.7143 | 96 | 18.9 | 6.9 | 25 | Y | 700
17/ | 11:00 | 1.19 | 85.7143 | 102 | 19.4 | 6.9 | 25 | Y | 700
18/ | 9:00 | 1.14 | 85.7143 | 97.7143 | 20.5 | 6.9 | 19 | Y | 700
19/ | 9:00 | 1.18 | 85.7143 | 101.1429 | 20.8 | 6.9 | 19 | Y | 700
20/ | 9:00 | 1.16 | 85.7143 | 99.4286 | 20 | 6.9 | 19 | Y | 700
21/ | 8:00 | 1.14 | 85.7143 | 97.7143 | 19.9 | 6.9 | 25 | Y | 700
22/ | 9:00 | 1.14 | 85.7143 | 97.7143 | 19.8 | 6.9 | 25 | Y | 700
23/ | 9:00 | 1.19 | 85.7143 | 102 | 19.7 | 6.9 | 25 | Y | 700
24/ | 9:00 | 1.2 | 85.7143 | 102.8571 | 19.8 | 6.9 | 25 | Y | 700
25/ | 9:00 | 1.11 | 85.7143 | 95.1429 | 19.8 | 6.9 | 25 | Y | 700
26/ | 9:00 | 1.19 | 85.7143 | 102 | 19.7 | 6.9 | 25 | Y | 700
27/ | 9:00 | 1.14 | 85.7143 | 97.7143 | 20.3 | 6.9 | 19 | Y | 700
28/ | 7:00 | 1.14 | 85.7143 | 97.7143 | 18.9 | 6.9 | 25 | Y | 700
29/ | 9:00 | 1.11 | 85.7143 | 95.1429 | 18.2 | 6.9 | 25 | Y | 700
30/ | 9:00 | 1.08 | 85.7143 | 92.5714 | 18.8 | 6.9 | 25 | Y | 700
31/ | 9:00 | 1.1 | 85.7143 | 94.2857 | 19.4 | 6.9 | 25 | Y | 700
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2