## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2022-12-22
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | OFF | OFF | OFF | 0.28 | 0.1 | 0.06 | 0.28
2 | 0.04 | 0.06 | 0.04 | OFF | 0.04 | 0.05 | 0.22
3 | 0.05 | 0.04 | 0.06 | OFF | 0.04 | 0.03 | 0.12
4 | 0.11 | 0.04 | OFF | OFF | 0.03 | 0.04 | 0.11
5 | 0.04 | 0.04 | 0.05 | 0.04 | 0.03 | 0.08 | 0.1
6 | 0.03 | OFF | OFF | 0.04 | 0.05 | 0.04 | 0.08
7 | 0.05 | 0.11 | 0.04 | OFF | OFF | 0.03 | 0.1
8 | 0.04 | 0.04 | 0.03 | 0.06 | 0.04 | 0.04 | 0.12
9 | 0.05 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.14
10 | 0.05 | 0.06 | 0.07 | 0.1 | 0.07 | 0.06 | 0.28
11 | 0.09 | OFF | OFF | 0.05 | 0.04 | 0.03 | 0.14
12 | 0.04 | 0.04 | 0.03 | 0.04 | 0.04 | 0.03 | 0.12
13 | 0.04 | OFF | OFF | 0.04 | 0.03 | 0.06 | 0.1
14 | 0.04 | 0.04 | 0.06 | 0.04 | 0.04 | OFF | 0.09
15 | 0.04 | 0.04 | 0.03 | 0.04 | 0.04 | 0.03 | 0.1
16 | 0.04 | OFF | OFF | 0.03 | 0.05 | 0.06 | 0.09
17 | 0.03 | 0.04 | 0.05 | 0.03 | 0.03 | 0.04 | 0.09
18 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.03 | 0.09
19 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.1
20 | 0.04 | OFF | OFF | 0.09 | 0.04 | 0.03 | 0.1
21 | 0.04 | 0.03 | 0.04 | 0.04 | 0.04 | 0.04 | 0.1
22 | 0.04 | OFF | OFF | 0.04 | 0.03 | 0.05 | 0.1
23 | 0.04 | 0.1 | 0.04 | 0.04 | 0.05 | 0.05 | 0.11
24 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.23
25 | 0.1 | 0.07 | 0.09 | 0.04 | 0.05 | 0.07 | 0.25
26 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.12 | 0.12
27 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
28 | OFF | OFF | OFF | 0.23 | 0.06 | 0.23 | 0.23
29 | 0.15 | 0.05 | OFF | 0.04 | 0.09 | 0.15 | 0.15
30 | OFF | OFF | 0.06 | 0.14 | OFF | 0.14 | 0.14
31 | 0.04 | OFF | 0.04 | 0.04 | 0.03 | 0.05 | 0.05
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2023-01-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2022-12-22 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.02 | 150 | 153 | 8.5 | 6.8 | 25 | Y | 400
2 / | 9:00 | 1.32 | 150 | 198 | 6.6 | 7 | 26 | Y | 400
3 / | 8:00 | 1.36 | 150 | 204 | 6.9 | 6.8 | 26 | Y | 400
4 / | 8:00 | 1.33 | 150 | 199.5 | 6.6 | 6.9 | 26 | Y | 400
5 / | 9:00 | 1.33 | 150 | 199.5 | 6.3 | 7 | 26 | Y | 400
6 / | 9:00 | 1.37 | 150 | 205.5 | 6.2 | 6.9 | 26 | Y | 400
7 / | 9:00 | 1.36 | 150 | 204 | 6.1 | 6.8 | 26 | Y | 400
8 / | 11:00 | 1.38 | 150 | 207 | 6.1 | 6.9 | 26 | Y | 400
9 / | 9:00 | 1.32 | 150 | 198 | 7.1 | 6.8 | 26 | Y | 400
10/ | 9:00 | 1.28 | 150 | 192 | 6.8 | 6.9 | 26 | Y | 400
11/ | 9:00 | 1.05 | 150 | 157.5 | 8 | 6.9 | 25 | Y | 400
12/ | 9:00 | 1.33 | 150 | 199.5 | 7.7 | 6.8 | 26 | Y | 400
13/ | 9:00 | 1.27 | 150 | 190.5 | 7.9 | 6.8 | 26 | Y | 400
14/ | 9:00 | 1.36 | 150 | 204 | 6.3 | 6.9 | 26 | Y | 400
15/ | 9:00 | 1.35 | 150 | 202.5 | 5.2 | 6.8 | 26 | Y | 400
16/ | 9:00 | 1.32 | 150 | 198 | 5.3 | 6.8 | 26 | Y | 400
17/ | 8:00 | 1.41 | 150 | 211.5 | 4.3 | 6.9 | 38 | Y | 400
18/ | 9:00 | 1.32 | 150 | 198 | 6 | 6.8 | 26 | Y | 400
19/ | 9:00 | 1.34 | 150 | 201 | 5.7 | 6.8 | 26 | Y | 400
20/ | 9:00 | 1.33 | 150 | 199.5 | 6.6 | 6.8 | 26 | Y | 400
21/ | 9:00 | 1.36 | 150 | 204 | 6.5 | 6.8 | 26 | Y | 400
22/ | 10:00 | 1.26 | 150 | 189 | 6.1 | 6.8 | 26 | Y | 400
23/ | 9:00 | 1.35 | 150 | 202.5 | 3.3 | 6.8 | 37 | Y | 400
24/ | 8:00 | 1.28 | 150 | 192 | 5 | 6.8 | 26 | Y | 400
25/ | 9:00 | 1.14 | 150 | 171 | 5.4 | 6.9 | 25 | Y | 400
26/ | 9:00 | 1.24 | 150 | 186 | 7 | 7 | 26 | Y | 400
27/ | 9:00 | 1.11 | 0 | 0 | 8 | 7 | 0 | Y | 0
28/ | 9:00 | 0.96 | 150 | 144 | 8.1 | 7 | 25 | Y | 400
29/ | 9:00 | 1.26 | 150 | 189 | 8.3 | 6.8 | 26 | Y | 400
30/ | 9:00 | 1.38 | 150 | 207 | 8.5 | 6.8 | 26 | Y | 400
31/ | 8:00 | 1.23 | 150 | 184.5 | 8.5 | 6.8 | 26 | Y | 400
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2