## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2023-03-23
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.04 | 0.04 | 0.05 | 0.04 | 0.03 | 0.04 | 0.14
2 | 0.04 | 0.04 | 0.08 | 0.04 | 0.04 | 0.04 | 0.11
3 | 0.05 | 0.04 | 0.04 | OFF | OFF | 0.07 | 0.1
4 | 0.04 | 0.04 | 0.03 | 0.05 | 0.04 | 0.04 | 0.1
5 | 0.04 | 0.05 | OFF | 0.05 | 0.04 | 0.05 | 0.12
6 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.1
7 | 0.08 | 0.05 | OFF | 0.04 | 0.04 | 0.05 | 0.1
8 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.09
9 | 0.04 | 0.06 | 0.04 | 0.04 | 0.04 | 0.04 | 0.08
10 | 0.04 | OFF | OFF | 0.1 | 0.09 | 0.05 | 0.18
11 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.12
12 | 0.04 | 0.03 | OFF | 0.04 | 0.04 | 0.04 | 0.09
13 | 0.04 | 0.03 | 0.14 | OFF | OFF | OFF | 0.14
14 | OFF | OFF | OFF | 0.05 | 0.04 | OFF | 0.24
15 | 0.04 | 0.04 | 0.03 | 0.09 | 0.05 | 0.04 | 0.12
16 | 0.05 | OFF | 0.06 | 0.08 | 0.04 | 0.04 | 0.1
17 | 0.04 | 0.04 | 0.04 | 0.04 | 0.08 | 0.06 | 0.08
18 | 0.03 | OFF | OFF | 0.03 | 0.05 | 0.03 | 0.08
19 | 0.04 | 0.03 | OFF | OFF | 0.03 | 0.03 | 0.08
20 | 0.04 | 0.04 | 0.04 | 0.03 | 0.08 | OFF | 0.08
21 | 0.04 | 0.04 | 0.04 | 0.05 | 0.04 | 0.04 | 0.08
22 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.1
23 | 0.04 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.08
24 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.08
25 | 0.04 | 0.06 | OFF | OFF | 0.04 | 0.04 | 0.13
26 | 0.13 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.13
27 | 0.04 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.1
28 | 0.03 | 0.03 | OFF | 0.04 | 0.04 | 0.06 | 0.11
29 | 0.03 | 0.03 | 0.03 | 0.1 | 0.04 | 0.04 | 0.1
30 | 0.04 | OFF | OFF | OFF | OFF | OFF | 0.1
31 | OFF | OFF | OFF | 0.05 | 0.04 | 0.03 | 0.09
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2023-04-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2023-03-23 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.25 | 150 | 187.5 | 5.4 | 7 | 26 | Y | 400
2 / | 10:00 | 1.3 | 150 | 195 | 6 | 7 | 26 | Y | 400
3 / | 9:00 | 1.27 | 150 | 190.5 | 6 | 7 | 26 | Y | 400
4 / | 9:00 | 1.26 | 150 | 189 | 6.4 | 7 | 26 | Y | 400
5 / | 9:00 | 1.13 | 150 | 169.5 | 6.5 | 7 | 25 | Y | 400
6 / | 10:00 | 1.25 | 150 | 187.5 | 6.2 | 7 | 26 | Y | 400
7 / | 9:00 | 1.29 | 150 | 193.5 | 6.9 | 7 | 26 | Y | 400
8 / | 9:00 | 1.29 | 150 | 193.5 | 6.2 | 7 | 26 | Y | 400
9 / | 9:00 | 1.27 | 150 | 190.5 | 6.4 | 7 | 26 | Y | 400
10/ | 9:00 | 1.19 | 150 | 178.5 | 6.7 | 7 | 25 | Y | 400
11/ | 9:00 | 1.27 | 150 | 190.5 | 6.7 | 7 | 26 | Y | 400
12/ | 8:00 | 1.25 | 150 | 187.5 | 7 | 7 | 26 | Y | 400
13/ | 9:00 | 1.29 | 150 | 193.5 | 7.5 | 7 | 26 | Y | 400
14/ | 10:00 | 1.14 | 150 | 171 | 7.2 | 7 | 25 | Y | 400
15/ | 9:00 | 1.33 | 150 | 199.5 | 7 | 7 | 26 | Y | 400
16/ | 9:00 | 1.26 | 150 | 189 | 7.1 | 6.9 | 26 | Y | 400
17/ | 9:00 | 1.29 | 150 | 193.5 | 7.2 | 6.9 | 26 | Y | 400
18/ | 8:00 | 1.24 | 150 | 186 | 7.6 | 7 | 26 | Y | 400
19/ | 8:00 | 1.17 | 150 | 175.5 | 8 | 7.1 | 31 | Y | 400
20/ | 9:00 | 1.34 | 150 | 201 | 8.1 | 7.2 | 31 | Y | 400
21/ | 9:00 | 1.31 | 150 | 196.5 | 7.6 | 7.1 | 31 | Y | 400
22/ | 9:00 | 1.27 | 150 | 190.5 | 8.1 | 7 | 26 | Y | 400
23/ | 9:00 | 1.29 | 150 | 193.5 | 8.3 | 7.1 | 31 | Y | 400
24/ | 8:00 | 1.27 | 150 | 190.5 | 7.9 | 7.1 | 31 | Y | 400
25/ | 10:00 | 1.3 | 150 | 195 | 7.4 | 7.1 | 31 | Y | 400
26/ | 9:00 | 1.27 | 150 | 190.5 | 7.9 | 7.1 | 31 | Y | 400
27/ | 9:00 | 1.25 | 150 | 187.5 | 7.1 | 7 | 26 | Y | 400
28/ | 9:00 | 1.26 | 150 | 189 | 7.4 | 7 | 26 | Y | 400
29/ | 8:00 | 1.36 | 150 | 204 | 7 | 7.1 | 31 | Y | 400
30/ | 6:00 | 1.23 | 150 | 184.5 | 7.9 | 7.1 | 31 | Y | 400
31/ | 12:00 | 1.25 | 150 | 187.5 | 7.6 | 7.1 | 31 | Y | 400
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2