## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2023-05-23
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.04 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.1
2 | OFF | OFF | 0.04 | 0.03 | 0.04 | OFF | 0.1
3 | 0.04 | OFF | OFF | 0.04 | 0.03 | OFF | 0.07
4 | 0.05 | 0.04 | OFF | 0.04 | OFF | OFF | 0.09
5 | 0.04 | OFF | OFF | 0.06 | 0.04 | 0.04 | 0.1
6 | OFF | OFF | 0.03 | 0.05 | 0.04 | OFF | 0.08
7 | OFF | 0.03 | OFF | 0.04 | 0.03 | 0.04 | 0.09
8 | OFF | OFF | 0.03 | 0.03 | 0.03 | 0.05 | 0.11
9 | 0.06 | OFF | 0.03 | 0.04 | 0.03 | 0.04 | 0.11
10 | 0.04 | OFF | 0.04 | 0.04 | 0.04 | 0.04 | 0.11
11 | OFF | OFF | 0.03 | 0.03 | 0.04 | 0.1 | 0.11
12 | 0.04 | OFF | 0.03 | 0.04 | 0.04 | 0.04 | 0.1
13 | 0.05 | OFF | 0.03 | 0.04 | 0.04 | 0.04 | 0.1
14 | 0.05 | OFF | 0.06 | 0.04 | 0.04 | 0.04 | 0.1
15 | 0.05 | OFF | 0.05 | 0.04 | 0.04 | 0.06 | 0.1
16 | 0.07 | OFF | 0.05 | 0.06 | 0.05 | 0.07 | 0.1
17 | 0.05 | OFF | 0.05 | 0.08 | 0.05 | 0.04 | 0.1
18 | 0.05 | OFF | 0.07 | OFF | 0.04 | 0.05 | 0.1
19 | 0.04 | 0.07 | 0.05 | 0.04 | 0.05 | 0.04 | 0.09
20 | 0.04 | OFF | 0.04 | 0.04 | 0.04 | 0.06 | 0.08
21 | 0.05 | OFF | 0.04 | 0.04 | 0.05 | 0.04 | 0.08
22 | 0.08 | OFF | 0.03 | 0.05 | 0.04 | 0.05 | 0.12
23 | 0.06 | OFF | 0.05 | 0.04 | 0.04 | 0.04 | 0.1
24 | 0.04 | 0.04 | 0.12 | 0.04 | 0.04 | 0.04 | 0.12
25 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.09
26 | 0.04 | OFF | 0.04 | 0.04 | 0.04 | 0.04 | 0.1
27 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.04 | 0.08
28 | 0.05 | OFF | 0.04 | 0.03 | 0.04 | 0.04 | 0.08
29 | 0.04 | OFF | 0.08 | 0.04 | 0.04 | 0.04 | 0.08
30 | 0.04 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.08
31 | 0.07 | 0.04 | 0.04 | 0.08 | 0.04 | 0.04 | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2023-06-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2023-05-23 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.24 | 100 | 124 | 11.6 | 7 | 19 | Y | 600
2 / | 9:00 | 1.21 | 100 | 121 | 11.6 | 7 | 19 | Y | 600
3 / | 9:00 | 1.24 | 100 | 124 | 11.3 | 7 | 19 | Y | 600
4 / | 9:00 | 1.26 | 100 | 126 | 11.8 | 7 | 19 | Y | 600
5 / | 9:00 | 1.24 | 100 | 124 | 11.1 | 7 | 19 | Y | 600
6 / | 8:00 | 1.27 | 100 | 127 | 11.1 | 7 | 19 | Y | 600
7 / | 8:00 | 1.07 | 100 | 107 | 11.1 | 6.8 | 19 | Y | 600
8 / | 9:00 | 1.25 | 100 | 125 | 11.4 | 6.8 | 19 | Y | 600
9 / | 9:00 | 1.36 | 100 | 136 | 10.6 | 7 | 19 | Y | 600
10/ | 9:00 | 1.26 | 100 | 126 | 11.3 | 6.9 | 19 | Y | 600
11/ | 10:00 | 1.29 | 100 | 129 | 12 | 6.9 | 19 | Y | 600
12/ | 9:00 | 1.21 | 100 | 121 | 13.1 | 6.9 | 19 | Y | 600
13/ | 9:00 | 1.23 | 100 | 123 | 13.3 | 6.9 | 19 | Y | 600
14/ | 7:00 | 1.1 | 100 | 110 | 13.7 | 6.9 | 19 | Y | 600
15/ | 8:00 | 1.1 | 100 | 110 | 14.4 | 6.9 | 19 | Y | 600
16/ | 9:00 | 1.13 | 100 | 113 | 16.2 | 6.9 | 13 | Y | 600
17/ | 9:00 | 1.17 | 100 | 117 | 16.3 | 6.9 | 13 | Y | 600
18/ | 9:00 | 1.15 | 100 | 115 | 16.6 | 6.9 | 13 | Y | 600
19/ | 9:00 | 1.21 | 100 | 121 | 15.7 | 6.9 | 13 | Y | 600
20/ | 8:00 | 1.23 | 100 | 123 | 16 | 7 | 13 | Y | 600
21/ | 8:00 | 1.18 | 100 | 118 | 15.9 | 6.9 | 13 | Y | 600
22/ | 9:00 | 1.26 | 100 | 126 | 15 | 6.9 | 13 | Y | 600
23/ | 9:00 | 1.24 | 100 | 124 | 13.6 | 6.9 | 19 | Y | 600
24/ | 9:00 | 1.3 | 100 | 130 | 13 | 6.9 | 19 | Y | 600
25/ | 9:00 | 1.27 | 100 | 127 | 13.9 | 6.9 | 19 | Y | 600
26/ | 8:00 | 1.3 | 100 | 130 | 14.4 | 6.9 | 19 | Y | 600
27/ | 8:00 | 1.18 | 100 | 118 | 15.4 | 6.9 | 13 | Y | 600
28/ | 9:00 | 1.21 | 100 | 121 | 14.9 | 6.9 | 19 | Y | 600
29/ | 9:00 | 1.21 | 100 | 121 | 15 | 6.9 | 13 | Y | 600
30/ | 9:00 | 1.09 | 90.9091 | 99.0909 | 15 | 7 | 13 | Y | 660
31/ | 9:00 | 1.3 | 88.2353 | 114.7059 | 13.8 | 7 | 19 | Y | 680
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2