## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2023-07-23
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.07 | 0.06 | 0.05 | 0.06 | 0.06 | 0.06 | 0.1
2 | 0.12 | 0.08 | 0.06 | 0.06 | 0.06 | 0.06 | 0.12
3 | 0.07 | OFF | 0.07 | 0.06 | 0.06 | 0.07 | 0.12
4 | 0.04 | OFF | 0.07 | 0.07 | 0.07 | 0.07 | 0.12
5 | 0.09 | 0.08 | 0.07 | 0.08 | 0.08 | 0.08 | 0.14
6 | 0.09 | OFF | 0.08 | 0.12 | 0.08 | 0.08 | 0.12
7 | 0.14 | OFF | 0.12 | 0.07 | 0.09 | 0.08 | 0.14
8 | 0.07 | OFF | 0.08 | 0.07 | 0.06 | 0.08 | 0.14
9 | 0.07 | OFF | 0.06 | 0.08 | 0.07 | 0.06 | 0.16
10 | 0.08 | OFF | 0.15 | 0.06 | 0.08 | 0.08 | 0.15
11 | 0.07 | OFF | 0.07 | 0.08 | 0.07 | 0.08 | 0.13
12 | 0.08 | 0.07 | 0.07 | 0.07 | 0.08 | 0.08 | 0.13
13 | 0.09 | OFF | 0.07 | 0.1 | 0.08 | 0.08 | 0.13
14 | 0.08 | 0.08 | 0.07 | 0.09 | 0.08 | 0.08 | 0.14
15 | 0.08 | 0.08 | 0.1 | 0.08 | 0.08 | 0.1 | 0.14
16 | 0.08 | 0.08 | 0.09 | 0.08 | 0.09 | 0.09 | 0.15
17 | 0.1 | OFF | 0.14 | 0.09 | 0.1 | 0.1 | 0.16
18 | 0.09 | 0.1 | 0.09 | 0.08 | 0.1 | 0.09 | 0.16
19 | 0.1 | 0.12 | 0.08 | 0.1 | 0.11 | 0.09 | 0.15
20 | 0.09 | 0.09 | 0.14 | 0.09 | 0.08 | OFF | 0.18
21 | 0.1 | 0.09 | 0.1 | 0.09 | 0.16 | 0.16 | 0.16
22 | 0.09 | OFF | 0.09 | 0.11 | 0.09 | OFF | 0.14
23 | 0.1 | 0.09 | 0.08 | 0.11 | 0.09 | 0.09 | 0.15
24 | 0.09 | 0.12 | 0.09 | 0.1 | 0.09 | 0.16 | 0.16
25 | 0.1 | 0.08 | 0.1 | 0.09 | 0.09 | 0.1 | 0.13
26 | 0.12 | 0.09 | 0.08 | 0.11 | 0.12 | 0.09 | 0.12
27 | 0.09 | 0.09 | 0.1 | 0.08 | 0.11 | 0.09 | 0.12
28 | 0.09 | 0.09 | 0.08 | 0.1 | 0.1 | 0.09 | 0.12
29 | 0.09 | OFF | 0.08 | 0.08 | 0.08 | 0.1 | 0.15
30 | 0.1 | 0.08 | 0.1 | 0.09 | 0.08 | 0.1 | 0.19
31 | 0.13 | 0.1 | 0.1 | 0.09 | 0.11 | 0.1 | 0.14
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2023-08-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2023-07-23 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.23 | 72.2892 | 88.9157 | 19 | 7 | 26 | Y | 830
2 / | 8:00 | 1.09 | 72.2892 | 78.7952 | 18.8 | 7 | 25 | Y | 830
3 / | 9:00 | 1.25 | 72.2892 | 90.3614 | 18.8 | 7 | 26 | Y | 830
4 / | 9:00 | 1.21 | 72.2892 | 87.4699 | 19.2 | 7 | 26 | Y | 830
5 / | 9:00 | 1.23 | 72.2892 | 88.9157 | 19.6 | 7 | 26 | Y | 830
6 / | 9:00 | 1.28 | 72.2892 | 92.5301 | 19.9 | 7 | 26 | Y | 830
7 / | 9:00 | 1.3 | 72.2892 | 93.9759 | 19.4 | 7 | 26 | Y | 830
8 / | 8:00 | 1.31 | 72.2892 | 94.6988 | 18.6 | 7.1 | 31 | Y | 830
9 / | 8:00 | 1.27 | 72.2892 | 91.8072 | 18.1 | 7 | 26 | Y | 830
10/ | 9:00 | 1.29 | 72.2892 | 93.253 | 18.4 | 7 | 26 | Y | 830
11/ | 9:00 | 1.38 | 72.2892 | 99.759 | 17.6 | 7 | 26 | Y | 830
12/ | 9:00 | 1.3 | 66.6667 | 86.6667 | 18.3 | 7 | 26 | Y | 900
13/ | 9:00 | 1.29 | 66.6667 | 86 | 19 | 6.9 | 26 | Y | 900
14/ | 9:00 | 1.27 | 66.6667 | 84.6667 | 19.3 | 7 | 26 | Y | 900
15/ | 8:00 | 1.18 | 66.6667 | 78.6667 | 20.7 | 7 | 19 | Y | 900
16/ | 8:00 | 1.12 | 66.6667 | 74.6667 | 20.8 | 7 | 19 | Y | 900
17/ | 9:00 | 1.18 | 66.6667 | 78.6667 | 20.1 | 7 | 19 | Y | 900
18/ | 9:00 | 1.17 | 66.6667 | 78 | 19.2 | 7 | 26 | Y | 900
19/ | 9:00 | 1.28 | 66.6667 | 85.3333 | 19.6 | 7 | 26 | Y | 900
20/ | 9:00 | 1.19 | 66.6667 | 79.3333 | 19.9 | 7.1 | 31 | Y | 900
21/ | 9:00 | 1.28 | 66.6667 | 85.3333 | 20.1 | 7 | 19 | Y | 900
22/ | 8:00 | 1.19 | 66.6667 | 79.3333 | 20.2 | 7 | 19 | Y | 900
23/ | 9:00 | 1.14 | 66.6667 | 76 | 20 | 7 | 19 | Y | 900
24/ | 9:00 | 1.18 | 66.6667 | 78.6667 | 19.9 | 7.1 | 31 | Y | 900
25/ | 9:00 | 1.28 | 66.6667 | 85.3333 | 19.6 | 7 | 26 | Y | 900
26/ | 9:00 | 1.31 | 66.6667 | 87.3333 | 19.7 | 7 | 26 | Y | 900
27/ | 9:00 | 1.28 | 66.6667 | 85.3333 | 19.9 | 7 | 26 | Y | 900
28/ | 9:00 | 1.27 | 66.6667 | 84.6667 | 19.6 | 7 | 26 | Y | 900
29/ | 8:00 | 1.24 | 66.6667 | 82.6667 | 19.4 | 7 | 26 | Y | 900
30/ | 10:00 | 1.14 | 66.6667 | 76 | 19.1 | 7 | 25 | Y | 900
31/ | 10:00 | 1.22 | 66.6667 | 81.3333 | 18.8 | 7 | 26 | Y | 900
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2