## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2023-08-23
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.11 | 0.1 | 0.09 | 0.1 | 0.1 | 0.18 | 0.18
2 | 0.11 | 0.1 | 0.09 | 0.08 | 0.1 | 0.09 | 0.18
3 | 0.1 | 0.09 | 0.12 | 0.09 | OFF | 0.09 | 0.18
4 | 0.11 | 0.1 | 0.09 | 0.12 | 0.11 | 0.1 | 0.15
5 | 0.1 | OFF | 0.11 | 0.09 | 0.09 | 0.11 | 0.13
6 | 0.1 | 0.09 | 0.1 | 0.09 | 0.15 | OFF | 0.15
7 | 0.11 | OFF | 0.11 | 0.09 | 0.11 | 0.11 | 0.18
8 | 0.14 | 0.11 | 0.1 | 0.1 | 0.1 | 0.11 | 0.17
9 | 0.09 | 0.1 | 0.1 | 0.09 | 0.11 | 0.11 | 0.17
10 | 0.11 | 0.1 | 0.1 | 0.1 | 0.14 | 0.11 | 0.16
11 | 0.11 | 0.09 | 0.1 | 0.09 | 0.13 | 0.11 | 0.16
12 | 0.15 | 0.11 | 0.09 | 0.11 | 0.1 | 0.11 | 0.15
13 | 0.11 | OFF | 0.1 | 0.09 | 0.11 | 0.14 | 0.18
14 | 0.12 | OFF | 0.09 | 0.1 | 0.1 | 0.13 | 0.16
15 | 0.14 | 0.1 | 0.12 | 0.1 | 0.12 | 0.11 | 0.17
16 | 0.17 | 0.11 | 0.1 | 0.11 | 0.11 | 0.14 | 0.18
17 | 0.14 | 0.1 | 0.15 | 0.09 | 0.12 | 0.11 | 0.17
18 | 0.15 | OFF | 0.11 | 0.13 | 0.12 | 0.11 | 0.18
19 | 0.14 | 0.22 | 0.14 | 0.09 | 0.11 | 0.1 | 0.22
20 | 0.1 | 0.13 | 0.12 | 0.09 | 0.1 | 0.1 | 0.18
21 | 0.11 | 0.11 | 0.11 | OFF | 0.11 | OFF | 0.21
22 | 0.11 | OFF | 0.12 | 0.1 | 0.14 | 0.11 | 0.17
23 | 0.12 | OFF | 0.09 | 0.09 | 0.09 | 0.08 | 0.16
24 | 0.1 | OFF | 0.09 | 0.08 | 0.14 | 0.1 | 0.15
25 | 0.1 | 0.09 | 0.12 | 0.11 | 0.14 | OFF | 0.18
26 | 0.1 | OFF | 0.09 | 0.11 | 0.11 | 0.11 | 0.17
27 | 0.11 | 0.1 | 0.11 | 0.11 | 0.11 | 0.11 | 0.16
28 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.11 | 0.16
29 | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.13 | 0.18
30 | 0.12 | 0.12 | 0.12 | 0.12 | 0.12 | 0.14 | 0.17
31 | 0.15 | 0.18 | OFF | OFF | 0.18 | 0.18 | 0.21
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2023-09-01
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2023-08-23 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.23 | 66.6667 | 82 | 19 | 7 | 26 | Y | 900
2 / | 9:00 | 1.25 | 66.6667 | 83.3333 | 19.4 | 7 | 26 | Y | 900
3 / | 9:00 | 1.16 | 66.6667 | 77.3333 | 19.7 | 7 | 25 | Y | 900
4 / | 9:00 | 1.21 | 66.6667 | 80.6667 | 19.7 | 7 | 26 | Y | 900
5 / | 9:00 | 1.2 | 66.6667 | 80 | 20.5 | 7 | 19 | Y | 900
6 / | 8:00 | 1.17 | 66.6667 | 78 | 20.1 | 7 | 19 | Y | 900
7 / | 8:00 | 1.24 | 66.6667 | 82.6667 | 20.7 | 7 | 19 | Y | 900
8 / | 8:00 | 1.08 | 66.6667 | 72 | 20.6 | 7 | 19 | Y | 900
9 / | 9:00 | 1.15 | 66.6667 | 76.6667 | 20.3 | 7.1 | 23 | Y | 900
10/ | 9:00 | 1.21 | 66.6667 | 80.6667 | 20.1 | 7 | 19 | Y | 900
11/ | 9:00 | 1.26 | 66.6667 | 84 | 20.2 | 7 | 19 | Y | 900
12/ | 8:00 | 1.09 | 66.6667 | 72.6667 | 20.3 | 7 | 19 | Y | 900
13/ | 9:00 | 1.09 | 66.6667 | 72.6667 | 20.6 | 7 | 19 | Y | 900
14/ | 9:00 | 1.01 | 66.6667 | 67.3333 | 21.6 | 7 | 19 | Y | 900
15/ | 7:00 | 1.01 | 66.6667 | 67.3333 | 22.4 | 7.1 | 23 | Y | 900
16/ | 8:00 | 1.09 | 66.6667 | 72.6667 | 22.7 | 7.1 | 23 | Y | 900
17/ | 7:00 | 1.06 | 66.6667 | 70.6667 | 23.1 | 7.1 | 23 | Y | 900
18/ | 8:00 | 1.11 | 66.6667 | 74 | 21.6 | 7.1 | 23 | Y | 900
19/ | 7:00 | 1.12 | 66.6667 | 74.6667 | 20.4 | 7.1 | 23 | Y | 900
20/ | 8:00 | 1.17 | 66.6667 | 78 | 20 | 7.1 | 23 | Y | 900
21/ | 9:00 | 1.25 | 66.6667 | 83.3333 | 19 | 7.1 | 31 | Y | 900
22/ | 9:00 | 1.32 | 66.6667 | 88 | 18.5 | 7.1 | 31 | Y | 900
23/ | 8:00 | 1.32 | 66.6667 | 88 | 17.9 | 7 | 26 | Y | 900
24/ | 8:00 | 1.28 | 66.6667 | 85.3333 | 18.4 | 7.1 | 31 | Y | 900
25/ | 9:00 | 1.34 | 66.6667 | 89.3333 | 18.6 | 7.1 | 31 | Y | 900
26/ | 8:00 | 1.18 | 125 | 147.5 | 19.3 | 7.1 | 15 | Y | 480
27/ | 10:00 | 0.85 | 125 | 106.25 | 19.5 | 7.2 | 15 | Y | 480
28/ | 10:00 | 0.8 | 125 | 100 | 18.9 | 7.2 | 15 | Y | 480
29/ | 8:00 | 1.12 | 125 | 140 | 18.3 | 7.1 | 15 | Y | 480
30/ | 9:00 | 1.18 | 125 | 147.5 | 18.7 | 7.1 | 15 | Y | 480
31/ | 9:00 | 1.12 | 125 | 140 | 18.5 | 7.1 | 15 | Y | 480
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2