## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2024-01-01
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.05 | 0.03 | OFF | 0.03 | 0.09 | 0.04 | 0.09
2 | 0.04 | 0.08 | 0.04 | 0.04 | 0.08 | 0.04 | 0.09
3 | 0.04 | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.1
4 | 0.04 | 0.04 | 0.04 | 0.05 | OFF | OFF | 0.1
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
7 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
8 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | OFF | OFF | OFF | OFF | 0.05 | 0.04 | 0.15
11 | 0.08 | 0.05 | OFF | 0.04 | 0.05 | 0.04 | 0.14
12 | 0.04 | OFF | OFF | 0.04 | 0.04 | 0.06 | 0.12
13 | 0.04 | OFF | OFF | 0.03 | 0.06 | 0.04 | 0.12
14 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
15 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
16 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
17 | OFF | OFF | OFF | 0.06 | 0.04 | 0.08 | 0.14
18 | 0.06 | 0.04 | 0.1 | 0.06 | 0.05 | 0.08 | 0.21
19 | OFF | OFF | OFF | 0.04 | OFF | 0.07 | 0.16
20 | 0.04 | 0.04 | OFF | 0.08 | 0.04 | 0.04 | 0.18
21 | 0.07 | 0.09 | 0.04 | OFF | 0.05 | 0.04 | 0.12
22 | 0.04 | 0.06 | 0.06 | 0.04 | OFF | 0.09 | 0.18
23 | 0.16 | 0.05 | OFF | 0.05 | 0.05 | 0.04 | 0.18
24 | 0.06 | 0.04 | 0.03 | 0.03 | 0.06 | 0.03 | 0.11
25 | 0.04 | 0.07 | 0.04 | OFF | 0.04 | 0.04 | 0.12
26 | 0.03 | OFF | OFF | OFF | 0.04 | 0.04 | 0.12
27 | 0.05 | 0.04 | OFF | 0.04 | OFF | 0.05 | 0.14
28 | 0.04 | 0.03 | 0.06 | 0.04 | 0.04 | 0.04 | 0.11
29 | 0.04 | 0.04 | 0.05 | 0.03 | 0.04 | 0.04 | 0.1
30 | 0.04 | OFF | OFF | 0.04 | 0.03 | OFF | 0.05
31 | OFF | OFF | 0.04 | 0.04 | 0.03 | 0.04 | 0.08
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2024-02-04
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2024-01-01 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.25 | 150 | 187.5 | 9 | 6.9 | 26 | Y | 400
2 / | 9:00 | 1.34 | 150 | 201 | 8.8 | 6.9 | 26 | Y | 400
3 / | 9:00 | 1.34 | 150 | 201 | 8.9 | 6.9 | 26 | Y | 400
4 / | 10:00 | 1.37 | 150 | 205.5 | 8.3 | 7 | 26 | Y | 400
5 / | 9:00 | 1.24 | 0 | 0 | 8.2 | 7 | 0 | Y | 0
6 / | 9:00 | 0.88 | 0 | 0 | 8.2 | 7 | 0 | Y | 0
7 / | 2:00 | 0.85 | 0 | 0 | 9.9 | 7 | 0 | Y | 0
8 / | 8:00 | 0.74 | 0 | 0 | 9.9 | 7 | 0 | Y | 0
9 / | 11:00 | 0.67 | 0 | 0 | 10 | 7 | 0 | Y | 0
10/ | 11:00 | 0.36 | 150 | 54 | 8.8 | 7 | 23 | Y | 400
11/ | 9:00 | 1.29 | 150 | 193.5 | 8.2 | 6.8 | 26 | Y | 400
12/ | 9:00 | 1.31 | 150 | 196.5 | 8.4 | 6.9 | 26 | Y | 400
13/ | 9:00 | 1.17 | 150 | 175.5 | 8.1 | 6.9 | 25 | Y | 400
14/ | 9:00 | 0.91 | 0 | 0 | 9 | 6.9 | 0 | Y | 0
15/ | 9:00 | 0.88 | 0 | 0 | 9 | 6.9 | 0 | Y | 0
16/ | 4:00 | 0.62 | 0 | 0 | 9 | 6.9 | 0 | Y | 0
17/ | 11:00 | 1.11 | 150 | 166.5 | 7.3 | 6.9 | 25 | Y | 400
18/ | 9:00 | 1.23 | 150 | 184.5 | 6.2 | 7.1 | 31 | Y | 400
19/ | 9:00 | 1.05 | 150 | 157.5 | 7 | 7.1 | 31 | Y | 400
20/ | 9:00 | 1.29 | 150 | 193.5 | 7.3 | 7.1 | 31 | Y | 400
21/ | 8:00 | 1.15 | 150 | 172.5 | 7.2 | 6.8 | 25 | Y | 400
22/ | 10:00 | 1.09 | 150 | 163.5 | 8 | 6.8 | 25 | Y | 400
23/ | 9:00 | 1.24 | 150 | 186 | 8.1 | 6.9 | 26 | Y | 400
24/ | 9:00 | 1.2 | 150 | 180 | 8.5 | 6.9 | 25 | Y | 400
25/ | 9:00 | 1.24 | 150 | 186 | 9.2 | 6.9 | 26 | Y | 400
26/ | 9:00 | 1.16 | 150 | 174 | 9 | 7 | 25 | Y | 400
27/ | 9:00 | 1.22 | 150 | 183 | 9.1 | 7 | 26 | Y | 400
28/ | 8:00 | 1.18 | 150 | 177 | 9.7 | 6.8 | 25 | Y | 400
29/ | 10:00 | 1.23 | 150 | 184.5 | 10.5 | 6.8 | 19 | Y | 400
30/ | 10:00 | 1.21 | 150 | 181.5 | 10.6 | 6.9 | 19 | Y | 400
31/ | 8:00 | 1.23 | 150 | 184.5 | 10.7 | 6.9 | 19 | Y | 400
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2