## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2024-05-24
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.09 | 0.09 | OFF | 0.1 | OFF | OFF | 0.1
2 | 0.05 | OFF | OFF | 0.05 | OFF | OFF | 0.2
3 | 0.05 | OFF | OFF | 0.05 | OFF | OFF | 0.19
4 | 0.06 | OFF | OFF | 0.2 | 0.38 | OFF | 0.55
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | OFF | 0.28 | 0.16 | 0.09 | 0.28
7 | 0.08 | OFF | 0.24 | 0.06 | 0.1 | 0.28 | 0.28
8 | OFF | OFF | 0.06 | 0.13 | 0.07 | 0.05 | 0.28
9 | 0.1 | OFF | 0.05 | 0.06 | 0.05 | 0.06 | 0.17
10 | OFF | 0.04 | OFF | 0.09 | 0.06 | OFF | 0.19
11 | 0.05 | OFF | 0.06 | 0.04 | 0.06 | OFF | 0.17
12 | OFF | 0.04 | OFF | 0.04 | 0.05 | OFF | 0.11
13 | 0.04 | OFF | 0.04 | 0.06 | 0.04 | 0.05 | 0.14
14 | 0.05 | 0.04 | 0.04 | 0.06 | 0.14 | 0.05 | 0.14
15 | OFF | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.08
16 | 0.05 | 0.04 | OFF | 0.06 | 0.04 | 0.04 | 0.12
17 | 0.06 | OFF | 0.04 | 0.11 | 0.05 | 0.04 | 0.11
18 | 0.04 | OFF | 0.04 | 0.04 | OFF | 0.04 | 0.14
19 | 0.04 | OFF | OFF | 0.03 | 0.06 | OFF | 0.12
20 | 0.08 | OFF | 0.07 | 0.06 | 0.04 | OFF | 0.16
21 | 0.03 | OFF | 0.04 | 0.07 | 0.12 | 0.09 | 0.12
22 | 0.05 | OFF | 0.04 | OFF | 0.08 | OFF | 0.12
23 | 0.04 | OFF | 0.04 | 0.06 | OFF | 0.04 | 0.12
24 | 0.06 | 0.06 | 0.05 | 0.05 | OFF | 0.1 | 0.12
25 | 0.04 | 0.04 | 0.04 | 0.05 | OFF | 0.04 | 0.1
26 | OFF | OFF | 0.04 | 0.05 | OFF | 0.04 | 0.09
27 | 0.04 | OFF | 0.05 | 0.04 | 0.05 | 0.05 | 0.12
28 | 0.05 | OFF | 0.05 | 0.05 | OFF | 0.04 | 0.12
29 | 0.06 | OFF | 0.06 | 0.04 | OFF | 0.04 | 0.12
30 | 0.05 | OFF | 0.06 | OFF | 0.07 | 0.06 | 0.1
31 | 0.05 | OFF | 0.07 | OFF | 0.14 | 0.05 | 0.14
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
Dennis W. Lewis
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | Dennis W Lewis T-6755 |  |  | 2024-06-02
|  |  |  | PHONE # |  |  | CERT # Level 4
|  |  |  | 1-541-929-3579 |  |  | WT-6755 FE
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2024-05-24 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 9:00 | 1.21 | 95.2381 | 115.2381 | 11.4 | 7.1 | 23 | Y | 630
2 / | 9:00 | 1.13 | 95.2381 | 107.619 | 11 | 7 | 19 | Y | 630
3 / | 9:00 | 1.19 | 95.2381 | 113.3333 | 11.3 | 7 | 19 | Y | 630
4 / | 8:00 | 1.09 | 95.2381 | 103.8095 | 11.2 | 7 | 19 | Y | 630
5 / | 8:00 | 0.86 | 0 | 0 | 11.9 | 7 | 0 | Y | 0
6 / | 9:00 | 1.1 | 95.2381 | 104.7619 | 10.7 | 7 | 19 | Y | 630
7 / | 9:00 | 1.18 | 95.2381 | 112.381 | 11 | 6.9 | 19 | Y | 630
8 / | 9:00 | 1.42 | 95.2381 | 135.2381 | 11 | 7 | 19 | Y | 630
9 / | 9:00 | 1.31 | 95.2381 | 124.7619 | 11.7 | 7 | 19 | Y | 630
10/ | 9:00 | 1.29 | 95.2381 | 122.8571 | 12.7 | 7 | 19 | Y | 630
11/ | 8:00 | 1.36 | 95.2381 | 129.5238 | 13.6 | 7 | 19 | Y | 630
12/ | 8:00 | 1.25 | 95.2381 | 119.0476 | 14.4 | 7 | 19 | Y | 630
13/ | 10:00 | 1.24 | 95.2381 | 118.0952 | 13.9 | 6.9 | 19 | Y | 630
14/ | 9:00 | 1.3 | 95.2381 | 123.8095 | 14.4 | 6.9 | 19 | Y | 630
15/ | 8:00 | 1.17 | 95.2381 | 111.4286 | 14.8 | 7 | 19 | Y | 630
16/ | 10:00 | 1.11 | 95.2381 | 105.7143 | 15 | 6.9 | 13 | Y | 630
17/ | 9:00 | 1.22 | 68.9655 | 84.1379 | 14.7 | 6.9 | 39 | Y | 870
18/ | 8:00 | 1.38 | 68.9655 | 95.1724 | 14.4 | 7 | 39 | Y | 870
19/ | 8:00 | 1.02 | 68.9655 | 70.3448 | 13.4 | 6.9 | 38 | Y | 870
20/ | 11:00 | 1.13 | 68.9655 | 77.931 | 12.5 | 6.9 | 38 | Y | 870
21/ | 9:00 | 1.11 | 68.9655 | 76.5517 | 13 | 7 | 38 | Y | 870
22/ | 9:00 | 1.21 | 68.9655 | 83.4483 | 12.5 | 7 | 39 | Y | 870
23/ | 9:00 | 1.21 | 68.9655 | 83.4483 | 12.7 | 7 | 39 | Y | 870
24/ | 9:00 | 1.24 | 68.9655 | 85.5172 | 13 | 7 | 39 | Y | 870
25/ | 8:00 | 1.23 | 68.9655 | 84.8276 | 12.5 | 7 | 39 | Y | 870
26/ | 7:00 | 1.17 | 68.9655 | 80.6897 | 11.8 | 7 | 38 | Y | 870
27/ | 8:00 | 1.12 | 68.9655 | 77.2414 | 11.9 | 7 | 38 | Y | 870
28/ | 8:00 | 1.14 | 68.9655 | 78.6207 | 13.1 | 7 | 38 | Y | 870
29/ | 9:00 | 1.21 | 68.9655 | 83.4483 | 13.3 | 7 | 39 | Y | 870
30/ | 8:00 | 1.18 | 68.9655 | 81.3793 | 13.5 | 7 | 38 | Y | 870
31/ | 9:00 | 1.16 | 68.9655 | 80 | 13.7 | 7 | 38 | Y | 870
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2