## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2024-08-24
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.09 | OFF | 0.07 | 0.08 | 0.08 | 0.08 | 0.14
2 | 0.11 | OFF | OFF | OFF | 0.14 | OFF | 0.14
3 | 0.1 | OFF | 0.1 | 0.08 | 0.08 | OFF | 0.12
4 | 0.14 | 0.08 | 0.08 | 0.07 | 0.1 | 0.08 | 0.14
5 | 0.09 | 0.08 | 0.07 | 0.12 | 0.08 | 0.08 | 0.12
6 | 0.14 | OFF | 0.08 | 0.08 | 0.08 | 0.09 | 0.18
7 | 0.09 | OFF | 0.08 | 0.08 | 0.11 | 0.08 | 0.14
8 | 0.09 | OFF | 0.08 | 0.08 | 0.09 | OFF | 0.14
9 | 0.08 | OFF | 0.1 | 0.08 | 0.1 | 0.09 | 0.15
10 | 0.1 | 0.09 | 0.08 | 0.09 | OFF | 0.09 | 0.16
11 | 0.13 | 0.16 | 0.1 | 0.08 | 0.08 | 0.11 | 0.16
12 | 0.09 | OFF | 0.09 | 0.09 | OFF | 0.09 | 0.15
13 | 0.11 | OFF | 0.13 | 0.08 | 0.12 | OFF | 0.17
14 | 0.1 | 0.09 | 0.09 | 0.08 | OFF | 0.08 | 0.18
15 | 0.1 | OFF | 0.09 | 0.08 | 0.15 | 0.1 | 0.15
16 | 0.08 | 0.09 | 0.09 | 0.09 | 0.13 | OFF | 0.16
17 | 0.1 | OFF | 0.08 | 0.09 | OFF | 0.1 | 0.13
18 | 0.12 | 0.1 | 0.11 | OFF | 0.1 | 0.1 | 0.18
19 | 0.15 | 0.09 | 0.08 | 0.08 | 0.11 | OFF | 0.16
20 | OFF | OFF | 0.08 | 0.08 | 0.09 | OFF | 0.17
21 | 0.08 | OFF | 0.09 | 0.13 | OFF | 0.06 | 0.15
22 | OFF | OFF | 0.07 | 0.13 | 0.07 | OFF | 0.14
23 | 0.07 | OFF | 0.08 | OFF | OFF | 0.06 | 0.17
24 | 0.09 | OFF | 0.07 | OFF | 0.07 | OFF | 0.13
25 | OFF | OFF | 0.06 | 0.07 | OFF | 0.06 | 0.15
26 | 0.08 | OFF | 0.07 | 0.06 | 0.07 | 0.09 | 0.13
27 | 0.07 | OFF | 0.08 | 0.07 | OFF | 0.09 | 0.15
28 | 0.07 | OFF | 0.09 | 0.06 | OFF | 0.08 | 0.15
29 | 0.07 | OFF | 0.09 | 0.07 | OFF | 0.09 | 0.14
30 | 0.09 | 0.08 | 0.06 | 0.09 | 0.07 | 0.07 | 0.16
31 | 0.06 | 0.07 | 0.07 | OFF | 0.16 | 0.08 | 0.16
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: | THOMAS | HOWARD
|  |  |  | SIGNATURE: | THOMAS | HOWARD | 2024-09-03
PHONE #
1-541-929-3579
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2024-08-24 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 10:00 | 1.18 | 68.9655 | 81.3793 | 20.4 | 7 | 19 | Y | 870
2 / | 9:00 | 1.2 | 68.9655 | 82.7586 | 21.3 | 7 | 19 | Y | 870
3 / | 8:00 | 1.18 | 68.9655 | 81.3793 | 21.6 | 7 | 19 | Y | 870
4 / | 9:00 | 1.18 | 68.9655 | 81.3793 | 20.7 | 7 | 19 | Y | 870
5 / | 8:00 | 1.14 | 68.9655 | 78.6207 | 20.4 | 7 | 19 | Y | 870
6 / | 9:00 | 1.04 | 68.9655 | 71.7241 | 20.2 | 7 | 19 | Y | 870
7 / | 9:00 | 1.05 | 68.9655 | 72.4138 | 19.6 | 7 | 25 | Y | 870
8 / | 11:00 | 1.03 | 68.9655 | 71.0345 | 20 | 7 | 19 | Y | 870
9 / | 9:00 | 1.11 | 68.9655 | 76.5517 | 20.6 | 7 | 19 | Y | 870
10/ | 8:00 | 1.14 | 68.9655 | 78.6207 | 20.3 | 7 | 19 | Y | 870
11/ | 10:00 | 1.15 | 69 | 79 | 20 | 7 | 19 | Y | 870
12/ | 9:00 | 1.17 | 69 | 80.73 | 19.7 | 7 | 25 | Y | 870
13/ | 9:00 | 1.14 | 69 | 78.66 | 19.1 | 7 | 25 | Y | 870
14/ | 9:00 | 0.96 | 69 | 66.24 | 18.4 | 7.1 | 30 | Y | 870
15/ | 9:00 | 1.18 | 69 | 81.42 | 19 | 7 | 25 | Y | 870
16/ | 9:00 | 1 | 69 | 69 | 19.4 | 7.1 | 30 | Y | 870
17/ | 8:00 | 1.14 | 69 | 78.66 | 19.1 | 7 | 25 | Y | 870
18/ | 8:00 | 1.03 | 68.9655 | 71.0345 | 18.7 | 7 | 25 | Y | 870
19/ | 8:00 | 1.13 | 68.9655 | 77.931 | 19 | 7 | 25 | Y | 870
20/ | 9:00 | 1.02 | 68.9655 | 70.3448 | 18.3 | 7 | 25 | Y | 870
21/ | 8:00 | 1.12 | 68.9655 | 77.2414 | 18.4 | 7.1 | 31 | Y | 870
22/ | 8:00 | 1.22 | 68.9655 | 84.1379 | 18 | 7.1 | 31 | y | 870
23/ | 8:00 | 1.13 | 68.9655 | 77.931 | 18 | 7.1 | 31 | y | 870
24/ | 8:00 | 1.16 | 68.9655 | 80 | 17.4 | 7 | 25 | y | 870
25/ | 8:00 | 1.23 | 68.9655 | 84.8276 | 16.7 | 6.9 | 26 | y | 870
26/ | 8:00 | 1.12 | 68.9655 | 77.2414 | 18 | 7 | 25 | y | 870
27/ | 8:00 | 1.18 | 68.9655 | 81.3793 | 18.6 | 7 | 25 | y | 870
28/ | 8:00 | 1.2 | 68.9655 | 82.7586 | 17.2 | 7.1 | 31 | y | 870
29/ | 8:00 | 1.13 | 68.9655 | 77.931 | 17.1 | 7.1 | 31 | y | 870
30/ | 8:00 | 1.18 | 68.9655 | 81.3793 | 17.6 | 7.1 | 31 | y | 870
31/ | 8:00 | 1.14 | 68.9655 | 78.6207 | 19 | 7.2 | 31 | y | 870
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2