## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Sept./2024
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.07 | 0.15 | 0.08 | 0.07 | off | 0.09 | 0.18
2 | off | off | 0.08 | 0.09 | off | 0.09 | 0.15
3 | 0.08 | off | 0.08 | 0.08 | 0.09 | off | 0.15
4 | 0.09 | off | 0.09 | 0.08 | 0.07 | 0.09 | 0.15
5 | 0.12 | off | 0.11 | off | off | 0.14 | 0.28
6 | 0.12 | off | 0.11 | 0.11 | 0.1 | 0.1 | 0.16
7 | 0.09 | off | 0.11 | 0.09 | 0.1 | off | 0.17
8 | 0.11 | 0.12 | 0.09 | 0.09 | 0.16 | 0.1 | 0.17
9 | off | 0.08 | 0.09 | off | off | 0.08 | 0.17
10 | off | off | 0.09 | 0.09 | off | 0.09 | 0.24
11 | off | off | 0.09 | 0.11 | off | 0.11 | 0.23
12 | off | off | 0.13 | off | 0.15 | 0.11 | 0.19
13 | 0.1 | off | 0.13 | 0.11 | off | 0.09 | 0.2
14 | off | 0.11 | 0.11 | off | 0.11 | off | 0.22
15 | 0.15 | 0.15 | 0.12 | 0.11 | 0.1 | 0.09 | 0.21
16 | off | 0.11 | 0.09 | off | 0.08 | off | 0.21
17 | 0.1 | off | 0.09 | off | 0.1 | off | 0.21
18 | 0.1 | off | 0.13 | off | 0.1 | 0.18 | 0.24
19 | 0.1 | 0.12 | 0.16 | 0.1 | off | 0.2 | 0.26
20 | off | 0.11 | 0.12 | off | 0.1 | off | 0.26
21 | 0.11 | off | 0.16 | off | 0.08 | off | 0.25
22 | 0.09 | off | 0.09 | 0.11 | off | 0.08 | 0.22
23 | 0.1 | 0.08 | 0.1 | 0.08 | off | 0.1 | 0.22
24 | 0.11 | off | 0.12 | off | off | 0.12 | 0.24
25 | off | 0.14 | 0.12 | off | off | off | 0.22
26 | off | off | off | 0.14 | 0.16 | off | 0.28
27 | 0.11 | off | 0.12 | off | 0.14 | 0.11 | 0.28
28 | 0.09 | off | 0.21 | 0.16 | 0.13 | 0.11 | 0.29
29 | 0.12 | off | 0.09 | 0.12 | 0.13 | 0.09 | 0.28
30 | 0.11 | 0.11 | 0.1 | 0.11 | 0.12 | 0.09 | 0.24
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | James Winge T-08175 |  |  | Oct. 2nd 2024
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Sept./2024 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.21 | 68.9655 | 83.4483 | 18.8 | 7.2 | 31 | yes | 870
2 / | 8:00 | 1.22 | 68.9655 | 84.1379 | 18.4 | 7.2 | 31 | yes | 870
3 / | 8:00 | 1.2 | 68.9655 | 82.7586 | 18 | 7.13 | 31 | yes | 870
4 / | 8:00 | 1.28 | 68.9655 | 88.2759 | 18.2 | 7.1 | 31 | yes | 870
5 / | 8:00 | 1.12 | 68.9655 | 77.2414 | 18.7 | 7.1 | 31 | yes | 870
6 / | 8:00 | 1.1 | 68.9655 | 75.8621 | 20.3 | 7.1 | 23 | yes | 870
7 / | 8:00 | 1.09 | 68.9655 | 75.1724 | 19.8 | 7.1 | 31 | yes | 870
8 / | 8:00 | 1 | 68.9655 | 68.9655 | 19.6 | 7.2 | 30 | yes | 870
9 / | 8:00 | 1.19 | 68.9655 | 82.069 | 19.3 | 7.1 | 31 | yes | 870
10/ | 8:00 | 1.15 | 68.9655 | 79.3103 | 19.4 | 7.1 | 31 | yes | 870
11/ | 8:00 | 1.13 | 68.9655 | 77.931 | 18.4 | 7.1 | 31 | yes | 870
12/ | 8:00 | 1.16 | 68.9655 | 80 | 18 | 7.2 | 31 | yes | 870
13/ | 8:00 | 1 | 68.9655 | 68.9655 | 17.2 | 7.2 | 30 | yes | 870
14/ | 8:00 | 1.01 | 68.9655 | 69.6552 | 18.5 | 7.2 | 31 | yes | 870
15/ | 8:00 | 1.11 | 68.9655 | 76.5517 | 18.4 | 7.3 | 31 | yes | 870
16/ | 8:00 | 1.18 | 68.9655 | 81.3793 | 17.6 | 7.1 | 31 | yes | 870
17/ | 8:00 | 0.94 | 68.9655 | 64.8276 | 16.8 | 7.1 | 30 | yes | 870
18/ | 8:00 | 1.09 | 68.9655 | 75.1724 | 16.4 | 7.1 | 31 | yes | 870
19/ | 8:00 | 0.89 | 68.9655 | 61.3793 | 16.6 | 7.2 | 30 | yes | 870
20/ | 8:00 | 1.08 | 68.9655 | 74.4828 | 16 | 7.23 | 31 | yes | 870
21/ | 8:00 | 0.97 | 68.9655 | 66.8966 | 16 | 7.2 | 30 | yes | 870
22/ | 8:00 | 0.97 | 68.9655 | 66.8966 | 15.4 | 7.3 | 30 | yes | 870
23/ | 8:00 | 1.14 | 68.9655 | 78.6207 | 16 | 7.2 | 31 | yes | 870
24/ | 8:00 | 1.17 | 68.9655 | 80.6897 | 17 | 7.1 | 31 | yes | 870
25/ | 8:00 | 1.15 | 68.9655 | 79.3103 | 17.3 | 7.2 | 31 | yes | 870
26/ | 8:00 | 0.99 | 68.9655 | 68.2759 | 17.2 | 7.2 | 30 | yes | 870
27/ | 8:00 | 1.04 | 68.9655 | 71.7241 | 16.4 | 7.2 | 15 | yes | 870
28/ | 8:00 | 0.95 | 120 | 114 | 17 | 7.1 | 15 | yes | 500
29/ | 8:00 | 1.02 | 120 | 122.4 | 16.2 | 7.2 | 15 | yes | 500
30/ | 8:00 | 1.38 | 120 | 165.6 | 15 | 7.2 | 16 | yes | 500
31/
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2