## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Oct.2024
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.11 | off | 0.21 | off | 0.12 | 0.21 | 0.24
2 | 0.09 | off | 0.09 | 0.09 | 0.11 | 0.14 | 0.16
3 | 0.12 | 0.1 | 0.1 | 0.11 | 0.12 | 0.1 | 0.2
4 | 0.11 | 0.14 | 0.1 | off | 0.09 | off | 0.2
5 | 0.13 | 0.12 | 0.12 | 0.09 | 0.08 | off | 0.28
6 | 0.12 | 0.12 | 0.08 | 0.12 | 0.14 | 0.1 | 0.28
7 | 0.07 | off | 0.07 | 0.08 | 0.08 | 0.07 | 0.22
8 | 0.08 | off | 0.08 | 0.09 | 0.09 | 0.09 | 0.17
9 | 0.09 | 0.1 | 0.1 | 0.08 | off | 0.12 | 0.2
10 | 0.1 | off | 0.1 | 0.16 | 0.09 | 0.1 | 0.23
11 | 0.1 | off | 0.1 | 0.08 | off | 0.09 | 0.18
12 | 0.11 | off | 0.07 | 0.09 | 0.08 | 0.11 | 0.24
13 | 0.08 | off | 0.1 | 0.09 | 0.11 | 0.08 | 0.2
14 | 0.09 | 0.1 | 0.09 | 0.08 | 0.18 | 0.1 | 0.22
15 | 0.08 | off | 0.1 | 0.11 | 0.11 | 0.1 | 0.24
16 | 0.12 | off | 0.11 | 0.11 | 0.11 | 0.12 | 0.23
17 | off | off | 0.2 | 0.16 | 0.12 | 0.14 | 0.28
18 | off | off | 0.15 | off | off | off | 0.28
19 | off | off | off | off | off | off | off
20 | off | off | off | off | off | off | off
21 | off | off | off | 0.14 | off | 0.12 | 0.28
22 | 0.28 | 0.12 | 0.28 | 0.11 | 0.28 | 0.09 | 0.28
23 | 0.09 | 0.14 | 0.09 | 0.1 | 0.1 | 0.2 | 0.22
24 | 0.2 | 0.1 | 0.14 | 0.12 | 0.1 | 0.07 | 0.28
25 | 0.16 | 0.08 | 0.16 | 0.14 | 0.28 | 0.07 | 0.28
26 | 0.1 | 0.16 | 0.07 | 0.08 | 0.09 | 0.28 | 0.28
27 | 0.08 | off | off | 0.28 | 0.26 | off | 0.28
28 | off | off | off | 0.28 | 0.14 | 0.13 | 0.28
29 | 0.12 | 0.11 | off | 0.09 | 0.12 | 0.09 | 0.28
30 | 0.14 | off | 0.28 | 0.07 | 0.1 | off | 0.28
31 | off | off | off | off | off | off | off
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME:
James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
|  |  |  | James Winge T-08175 |  |  | Nov. 6th 2024
PHONE #
1-541-929-3579
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Oct.2024 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.25 | 120 | 150 | 15.3 | 7.2 | 16 | Y | 500
2 / | 8:00 | 1.28 | 120 | 153.6 | 15.1 | 7.2 | 16 | Y | 500
3 / | 8:00 | 1.32 | 120 | 158.4 | 15.2 | 7.1 | 16 | Y | 500
4 / | 8:00 | 1.02 | 120 | 122.4 | 13.8 | 7.1 | 23 | Y | 500
5 / | 8:00 | 1.46 | 120 | 175.2 | 13.2 | 7.2 | 24 | Y | 500
6 / | 8:00 | 1.42 | 120 | 170.4 | 13 | 7.2 | 24 | Y | 500
7 / | 8:00 | 1.29 | 120 | 154.8 | 13.1 | 7.2 | 23 | Y | 500
8 / | 8:00 | 1.31 | 120 | 157.2 | 14.1 | 7.1 | 23 | Y | 500
9 / | 8:00 | 1.49 | 120 | 178.8 | 14.3 | 7.1 | 24 | Y | 500
10/ | 8:00 | 1.16 | 120 | 139.2 | 14.2 | 7.2 | 23 | Y | 500
11/ | 8:00 | 1.36 | 120 | 163.2 | 13.9 | 7.1 | 23 | Y | 500
12/ | 8:00 | 1.34 | 120 | 160.8 | 13.7 | 7.3 | 23 | Y | 500
13/ | 8:00 | 1.11 | 120 | 133.2 | 13.6 | 7.2 | 23 | Y | 500
14/ | 8:00 | 1.5 | 120 | 180 | 13.7 | 7.1 | 24 | Y | 500
15/ | 8:00 | 1.16 | 120 | 139.2 | 14.8 | 7.1 | 23 | Y | 500
16/ | 8:00 | 1.22 | 120 | 146.4 | 15.7 | 7.1 | 16 | Y | 500
17/ | 8:00 | 1 | 120 | 120 | 16 | 7.2 | 15 | Y | 500
18/ | 8:00 | 0.95 | 120 | 114 | 15 | 7.1 | 15 | Y | 500
19/ | 8:00 | 0.53 | 120 | 63.6 | 16 | 6.7 | 0 | Y | 500
20/ | 8:00 | 0.53 | 120 | 63.6 | 16.4 | 6.6 | 0 | Y | 500
21/ | 8:00 | 1.14 | 120 | 136.8 | 14.7 | 6.8 | 19 | Y | 500
22/ | 8:00 | 1.38 | 120 | 165.6 | 13.7 | 6.7 | 19 | Y | 500
23/ | 8:00 | 1.5 | 120 | 180 | 13 | 7 | 20 | Y | 500
24/ | 8:00 | 1.49 | 120 | 178.8 | 12.1 | 7.1 | 24 | Y | 500
25/ | 8:00 | 1.27 | 120 | 152.4 | 11.6 | 7.1 | 23 | Y | 500
26/ | 8:00 | 1.41 | 120 | 169.2 | 11.7 | 6.9 | 20 | Y | 500
27/ | 8:00 | 1.37 | 120 | 164.4 | 13.5 | 7.1 | 19 | Y | 500
28/ | 8:00 | 0.93 | 120 | 111.6 | 15.4 | 7.1 | 15 | Y | 500
29/ | 8:00 | 1.22 | 120 | 146.4 | 14 | 7.1 | 23 | Y | 500
30/ | 8:00 | 0.92 | 120 | 110.4 | 14.3 | 7.1 | 22 | Y | 500
31/ | 8:00 | 1 | 120 | 120 | 15.5 | 7.1 | 15 | Y | 500
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2