## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Nov. 2024
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
2 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
3 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
7 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
8 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
14 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
15 | OFF | OFF | 0.28 | 0.1 | 0.09 | 0.1 | 0.28
16 | 0.07 | OFF | OFF | 0.07 | 0.07 | 0.1 | 0.2
17 | 0.05 | OFF | OFF | 0.19 | 0.15 | 0.15 | 0.28
18 | 0.14 | OFF | OFF | OFF | OFF | OFF | 0.28
19 | OFF | OFF | 0.28 | 0.16 | 0.1 | 0.25 | 0.28
20 | OFF | OFF | 0.28 | 0.12 | OFF | OFF | 0.28
21 | OFF | OFF | 0.12 | OFF | 0.08 | 0.09 | 0.13
22 | 0.09 | OFF | OFF | 0.23 | 0.06 | 0.03 | 0.28
23 | 0.09 | OFF | OFF | 0.05 | 0.08 | 0.05 | 0.18
24 | 0.04 | OFF | 0.04 | 0.05 | 0.04 | 0.04 | 0.16
25 | 0.06 | OFF | OFF | 0.04 | 0.04 | 0.05 | 0.16
26 | 0.05 | OFF | 0.04 | 0.07 | 0.05 | 0.04 | 0.12
27 | OFF | 0.04 | 0.04 | 0.04 | OFF | 0.04 | 0.26
28 | 0.14 | 0.04 | OFF | 0.04 | 0.05 | 0.04 | 0.25
29 | 0.05 | OFF | 0.04 | 0.05 | 0.04 | 0.04 | 0.09
30 | OFF | OFF | 0.16 | 0.04 | 0.04 | 0.05 | 0.16
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge | e T-08175
WTP was off from the 1st trough the 14th
|  |  |  | SIGNATURE: | James Winge |  | DATE:12/03/2024
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Nov. 2024 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1 | 120 | 120 | 15.5 | 7.1 | 15 | YES | 500
2 / | 8:00 | 0.73 | OFF | OFF | 17 | 7.1 | OFF | OFF | OFF
3 / | 8:00 | 0.9 | OFF | OFF | 17.2 | 7.1 | OFF | OFF | OFF
4 / | 8:00 | 0.93 | OFF | OFF | 17.5 | 7.1 | OFF | OFF | OFF
5 / | 8:00 | 0.91 | OFF | OFF | 17.6 | 7.1 | OFF | OFF | OFF
6 / | 8:00 | 0.83 | OFF | OFF | 17.7 | 7.1 | OFF | OFF | OFF
7 / | 8:00 | 0.83 | OFF | OFF | 18 | 7.1 | OFF | OFF | OFF
8 / | 8:00 | 0.99 | OFF | OFF | 18 | 7.1 | OFF | OFF | OFF
9 / | 8:00 | 0.81 | OFF | OFF | 18 | 7.1 | OFF | OFF | OFF
10/ | 8:00 | 0.67 | OFF | OFF | 18.4 | 7.1 | OFF | OFF | OFF
11/ | 8:00 | 0.51 | OFF | OFF | 18.3 | 7.1 | OFF | OFF | OFF
12/ | 8:00 | 0.4 | OFF | OFF | 18.4 | 7.1 | OFF | OFF | OFF
13/ | 8:00 | 0.52 | 120 | 62.4 | 18.1 | 7.1 | 14 | YES | 500
14/ | 8:00 | 0.8 | OFF | OFF | 18 | 7.1 | OFF | OFF | OFF
15/ | 8:00 | 1.1 | 120 | 132 | 18 | 7.2 | 15 | YES | 500
16/ | 8:00 | 1.5 | 120 | 180 | 15 | 7.1 | 16 | YES | 500
17/ | 8:00 | 1.42 | 120 | 170.4 | 14.7 | 7 | 20 | YES | 500
18/ | 8:00 | 0.42 | 120 | 50.4 | 16.1 | 7 | 12 | YES | 500
19/ | 8:00 | 0.92 | 120 | 110.4 | 15.7 | 7 | 13 | YES | 500
20/ | 8:00 | 1.21 | 120 | 145.2 | 15.6 | 6.7 | 13 | YES | 500
21/ | 8:00 | 1.15 | 120 | 138 | 15.9 | 7.2 | 15 | YES | 500
22/ | 8:00 | 1.42 | 120 | 170.4 | 15.7 | 6.7 | 13 | YES | 500
23/ | 8:00 | 1.17 | 120 | 140.4 | 16.2 | 6.7 | 13 | YES | 500
24/ | 8:00 | 1.45 | 120 | 174 | 16 | 7.2 | 16 | YES | 500
25/ | 8:00 | 1.48 | 120 | 177.6 | 15.8 | 7.2 | 16 | YES | 500
26/ | 8:00 | 1.46 | 120 | 175.2 | 16 | 7.1 | 16 | YES | 500
27/ | 8:00 | 1.33 | 120 | 159.6 | 16 | 7.2 | 16 | YES | 500
28/ | 8:00 | 1.17 | 120 | 140.4 | 15.8 | 7.1 | 15 | YES | 500
29/ | 8:00 | 1.26 | 120 | 151.2 | 14.6 | 7 | 19 | YES | 500
30/ | 8:00 | 1.31 | 120 | 157.2 | 14.6 | 7 | 19 | YES | 500
31/ | 8:00 |  | #DIV/0! | #DIV/0!
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2