## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Dec. 2024
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.05 | OFF | OFF | 0.03 | 0.05 | 0.04 | 0.15
2 | 0.05 | 0.09 | OFF | 0.04 | 0.04 | 0.1 | 0.1
3 | 0.06 | OFF | 0.04 | 0.1 | 0.05 | 0.04 | 0.1
4 | OFF | OFF | 0.07 | 0.04 | 0.04 | 0.05 | 0.1
5 | 0.04 | OFF | OFF | 0.04 | 0.06 | 0.04 | 0.1
6 | 0.11 | OFF | 0.22 | 0.04 | 0.04 | 0.04 | 0.22
7 | 0.04 | OFF | OFF | 0.04 | 0.05 | 0.04 | 0.1
8 | 0.04 | 0.06 | 0.04 | 0.04 | 0.14 | 0.05 | 0.14
9 | 0.05 | 0.06 | 0.04 | 0.04 | 0.11 | 0.05 | 0.19
10 | 0.04 | OFF | 0.05 | 0.06 | 0.05 | 0.04 | 0.19
11 | 0.05 | OFF | 0.05 | 0.05 | 0.11 | 0.05 | 0.11
12 | 0.04 | OFF | 0.04 | 0.06 | 0.05 | 0.05 | 0.12
13 | 0.08 | OFF | 0.08 | 0.05 | 0.08 | 0.06 | 0.12
14 | 0.08 | OFF | OFF | 0.17 | 0.12 | 0.1 | 0.29
15 | 0.08 | 0.26 | OFF | 0.09 | 0.07 | 0.07 | 0.26
16 | 0.1 | OFF | OFF | 0.11 | 0.07 | 0.24 | 0.24
17 | OFF | OFF | 0.06 | 0.05 | 0.16 | 0.07 | 0.2
18 | OFF | 0.05 | OFF | 0.08 | 0.05 | 0.04 | 0.18
19 | 0.1 | 0.05 | 0.05 | 0.07 | 0.05 | 0.04 | 0.11
20 | 0.06 | OFF | 0.06 | 0.04 | 0.08 | 0.04 | 0.12
21 | 0.03 | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.09
22 | 0.06 | OFF | OFF | 0.06 | 0.04 | 0.04 | 0.09
23 | 0.1 | OFF | OFF | 0.04 | 0.05 | 0.05 | 0.12
24 | OFF | OFF | 0.04 | 0.05 | 0.05 | 0.05 | 0.12
25 | 0.05 | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.14
26 | 0.09 | OFF | OFF | 0.16 | OFF | 0.06 | 0.28
27 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
28 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
29 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
30 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
31 | OFF | OFF | OFF | 0.04 | OFF | 0.04 | 0.17
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
[5 empty] | James Winge |  | 2025-01-02
PHONE #
1-541-929-3579
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Dec. 2024 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.34 | 120 | 160.8 | 14.4 | 7 | 19 | Y | 500
2 / | 8:00 | 1.04 | 120 | 124.8 | 13.5 | 7.1 | 23 | Y | 500
3 / | 8:00 | 1.22 | 120 | 146.4 | 13 | 7 | 19 | Y | 500
4 / | 8:00 | 1.33 | 120 | 159.6 | 13 | 7 | 19 | Y | 500
5 / | 8:00 | 1.36 | 120 | 163.2 | 12.8 | 7 | 19 | Y | 500
6 / | 8:00 | 1.21 | 120 | 145.2 | 13.2 | 7 | 19 | Y | 500
7 / | 8:00 | 1.26 | 120 | 151.2 | 13.4 | 7 | 19 | Y | 500
8 / | 8:00 | 1.26 | 120 | 151.2 | 13.9 | 7 | 19 | Y | 500
9 / | 8:00 | 1.1 | 120 | 132 | 13.6 | 6.8 | 19 | Y | 500
10/ | 8:00 | 1.2 | 120 | 144 | 13.8 | 6.9 | 19 | Y | 500
11/ | 8:00 | 1.13 | 120 | 135.6 | 13.8 | 6.9 | 19 | Y | 500
12/ | 8:00 | 1.12 | 120 | 134.4 | 14 | 6.9 | 19 | Y | 500
13/ | 8:00 | 1.1 | 120 | 132 | 14 | 6.9 | 19 | Y | 500
14/ | 8:00 | 1.11 | 120 | 133.2 | 14.3 | 6.9 | 19 | Y | 500
15/ | 8:00 | 1.08 | 120 | 129.6 | 15 | 6.9 | 13 | Y | 500
16/ | 8:00 | 1 | 120 | 120 | 15.2 | 6.8 | 13 | Y | 500
17/ | 8:00 | 1.12 | 120 | 134.4 | 15 | 6.9 | 13 | Y | 500
18/ | 8:00 | 1.13 | 120 | 135.6 | 15.8 | 6.9 | 13 | Y | 500
19/ | 8:00 | 1.2 | 120 | 144 | 16.4 | 7.2 | 15 | Y | 500
20/ | 8:00 | 1.32 | 120 | 158.4 | 16.4 | 7 | 13 | Y | 500
21/ | 8:00 | 1.34 | 120 | 160.8 | 16 | 7 | 13 | Y | 500
22/ | 8:00 | 1.3 | 120 | 156 | 16.3 | 6.9 | 13 | Y | 500
23/ | 8:00 | 1.33 | 120 | 159.6 | 16.1 | 7.1 | 16 | Y | 500
24/ | 8:00 | 1.28 | 120 | 153.6 | 17.2 | 6.9 | 13 | Y | 500
25/ | 8:00 | 1.18 | 120 | 141.6 | 16 | 7.1 | 15 | Y | 500
26/ | 8:00 | 1.22 | 120 | 146.4 | 16.1 | 6.8 | 13 | Y | 500
27/ | 8:00 | 0.74 | #DIV/0! | #DIV/0! | 16.2 | 6.9 | OFF | Y | 0
28/ | 8:00 | 0.81 | #DIV/0! | #DIV/0! | 16.4 | 7 | OFF | Y | 0
29/ | 8:00 | 0.68 | #DIV/0! | #DIV/0! | 16.6 | 7 | OFF | Y | 0
30/ | 8:00 | 0.62 | #DIV/0! | #DIV/0! | 16.6 | 7 | OFF | Y | 0
31/ | 8:00 | 1.4 | 120 | 168 | 16.7 | 7 | 13 | Y | 500
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2