## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Jan. 2025
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.08 | OFF | OFF | 0.04 | 0.04 | 0.06 | 0.12
2 | 0.04 | OFF | 0.04 | 0.04 | 0.06 | 0.04 | 0.13
3 | OFF | OFF | 0.05 | 0.16 | 0.05 | OFF | 0.16
4 | 0.09 | 0.04 | 0.04 | OFF | 0.04 | 0.11 | 0.12
5 | 0.05 | OFF | OFF | 0.04 | 0.04 | 0.05 | 0.1
6 | 0.06 | OFF | 0.05 | 0.08 | 0.05 | 0.05 | 0.12
7 | OFF | 0.04 | 0.06 | OFF | 0.04 | 0.04 | 0.11
8 | 0.06 | OFF | OFF | 0.04 | OFF | 0.04 | 0.12
9 | 0.04 | OFF | OFF | 0.04 | 0.06 | 0.04 | 0.1
10 | OFF | 0.04 | 0.04 | 0.04 | 0.06 | 0.04 | 0.1
11 | 0.04 | OFF | OFF | 0.08 | 0.04 | 0.04 | 0.1
12 | 0.05 | OFF | OFF | 0.04 | 0.04 | 0.07 | 0.07
13 | 0.04 | OFF | OFF | 0.06 | 0.04 | 0.04 | 0.11
14 | 0.08 | OFF | 0.05 | 0.04 | 0.04 | 0.05 | 0.13
15 | 0.04 | OFF | 0.04 | 0.04 | 0.09 | 0.05 | 0.11
16 | OFF | OFF | 0.04 | 0.04 | 0.05 | 0.04 | 0.12
17 | 0.07 | OFF | 0.04 | 0.05 | 0.04 | 0.04 | 0.12
18 | OFF | OFF | 0.06 | 0.04 | 0.04 | 0.05 | 0.09
19 | 0.04 | OFF | OFF | 0.04 | 0.05 | 0.04 | 0.16
20 | 0.07 | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.16
21 | 0.14 | OFF | OFF | 0.04 | 0.07 | 0.05 | 0.28
22 | OFF | OFF | 0.04 | 0.06 | 0.05 | 0.08 | 0.28
23 | 0.06 | OFF | 0.04 | 0.04 | 0.04 | 0.05 | 0.14
24 | 0.03 | OFF | 0.04 | 0.04 | 0.04 | 0.04 | 0.1
25 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.04 | 0.09
26 | 0.05 | OFF | OFF | 0.04 | 0.04 | 0.05 | 0.09
27 | 0.05 | OFF | OFF | 0.04 | 0.07 | 0.04 | 0.09
28 | OFF | OFF | 0.04 | 0.08 | 0.04 | 0.04 | 0.12
29 | 0.03 | OFF | 0.07 | 0.04 | 0.04 | 0.1 | 0.1
30 | 0.03 | OFF | 0.04 | 0.04 | 0.05 | 0.05 | 0.1
31 | 0.04 | OFF | 0.04 | 0.07 | 0.04 | 0.05 | 0.12
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
[5 empty] | James Winge |  | 2025-02-01
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Jan. 2025 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.1 | 120 | 132 | 16 | 7 | 13 | YES | 500
2 / | 8:00 | 1.33 | 120 | 159.6 | 16 | 7.1 | 16 | YES | 500
3 / | 8:00 | 1.11 | 120 | 133.2 | 10 | 7 | 19 | YES | 500
4 / | 8:00 | 1.15 | 120 | 138 | 9.7 | 7 | 25 | YES | 500
5 / | 8:00 | 1.08 | 120 | 129.6 | 10.4 | 7 | 19 | YES | 500
6 / | 8:00 | 1.17 | 120 | 140.4 | 10.3 | 6.9 | 19 | YES | 500
7 / | 8:00 | 1.43 | 120 | 171.6 | 10 | 7 | 20 | YES | 500
8 / | 8:00 | 1.1 | 120 | 132 | 9.7 | 7 | 25 | YES | 500
9 / | 8:00 | 1.28 | 120 | 153.6 | 9.5 | 7.2 | 31 | YES | 500
10/ | 8:00 | 1.29 | 120 | 154.8 | 8.6 | 7 | 26 | YES | 500
11/ | 8:00 | 1.39 | 120 | 166.8 | 9.1 | 7 | 26 | YES | 500
12/ | 8:00 | 1.25 | 120 | 150 | 9.6 | 7 | 26 | YES | 500
13/ | 8:00 | 1.3 | 120 | 156 | 8.9 | 7.1 | 31 | YES | 500
14/ | 8:00 | 1.35 | 120 | 162 | 7.8 | 7.1 | 31 | YES | 500
15/ | 8:00 | 1.17 | 120 | 140.4 | 8 | 7 | 25 | YES | 500
16/ | 8:00 | 1.35 | 120 | 162 | 7.6 | 7.1 | 31 | YES | 500
17/ | 8:00 | 1.27 | 120 | 152.4 | 6.2 | 7 | 26 | YES | 500
18/ | 8:00 | 1.18 | 120 | 141.6 | 7 | 7 | 25 | YES | 500
19/ | 8:00 | 1.28 | 120 | 153.6 | 7.4 | 7 | 26 | YES | 500
20/ | 8:00 | 1.35 | 120 | 162 | 6 | 7 | 26 | YES | 500
21/ | 8:00 | 1.23 | 120 | 147.6 | 5.4 | 7.1 | 31 | YES | 500
22/ | 8:00 | 1.29 | 120 | 154.8 | 5.4 | 7.3 | 31 | YES | 500
23/ | 8:00 | 1.38 | 120 | 165.6 | 5.9 | 7 | 26 | YES | 500
24/ | 8:00 | 1.31 | 120 | 157.2 | 5.3 | 7.1 | 31 | YES | 500
25/ | 8:00 | 1.22 | 120 | 146.4 | 5.2 | 7 | 26 | YES | 500
26/ | 8:00 | 1.31 | 120 | 157.2 | 5.8 | 7 | 26 | YES | 500
27/ | 8:00 | 1.35 | 120 | 162 | 5.4 | 7.1 | 31 | YES | 500
28/ | 8:00 | 1.21 | 120 | 145.2 | 4.5 | 7.1 | 44 | YES | 500
29/ | 8:00 | 1.22 | 120 | 146.4 | 4.7 | 7.4 | 44 | YES | 500
30/ | 8:00 | 1.35 | 120 | 162 | 4.8 | 7.4 | 44 | YES | 500
31/ | 8:00 | 1.21 | 120 | 145.2 | 5.6 | 7.2 | 31 | YES | 500
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2