## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Mar. 2025
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.07 | OFF | OFF | 0.04 | 0.05 | 0.03 | 0.11
2 | 0.04 | OFF | OFF | 0.09 | 0.04 | 0.04 | 0.1
3 | OFF | OFF | OFF | 0.07 | 0.04 | 0.04 | 0.13
4 | OFF | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.17
5 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.04 | 0.14
6 | 0.04 | OFF | 0.04 | 0.04 | 0.07 | 0.04 | 0.14
7 | OFF | OFF | 0.04 | 0.04 | 0.04 | 0.04 | 0.14
8 | 0.05 | OFF | OFF | 0.04 | 0.04 | 0.05 | 0.13
9 | 0.04 | OFF | OFF | 0.04 | 0.05 | 0.04 | 0.14
10 | OFF | OFF | 0.04 | 0.06 | 0.04 | 0.04 | 0.12
11 | 0.05 | OFF | OFF | 0.04 | 0.05 | 0.06 | 0.12
12 | 0.04 | OFF | 0.04 | 0.05 | 0.06 | 0.04 | 0.12
13 | 0.07 | OFF | OFF | 0.08 | 0.05 | 0.06 | 0.14
14 | 0.07 | OFF | OFF | 0.05 | 0.05 | 0.07 | 0.19
15 | OFF | OFF | 0.05 | 0.09 | 0.14 | 0.06 | 0.28
16 | 0.09 | OFF | OFF | 0.13 | 0.05 | 0.07 | 0.29
17 | 0.16 | 0.24 | OFF | 0.05 | 0.04 | 0.07 | 0.28
18 | OFF | OFF | OFF | 0.05 | 0.06 | 0.06 | 0.2
19 | 0.05 | OFF | 0.05 | 0.04 | 0.06 | 0.05 | 0.12
20 | 0.04 | OFF | 0.04 | 0.05 | 0.05 | 0.04 | 0.15
21 | 0.06 | OFF | OFF | 0.05 | 0.04 | 0.07 | 0.18
22 | 0.07 | OFF | OFF | 0.04 | 0.05 | 0.05 | 0.18
23 | 0.05 | OFF | OFF | 0.05 | 0.04 | 0.04 | 0.1
24 | OFF | OFF | OFF | 0.06 | 0.04 | 0.04 | 0.12
25 | 0.08 | OFF | OFF | 0.04 | 0.05 | 0.04 | 0.11
26 | 0.04 | 0.06 | 0.05 | 0.04 | 0.04 | 0.05 | 0.1
27 | 0.06 | OFF | 0.06 | 0.04 | 0.06 | 0.04 | 0.11
28 | 0.07 | OFF | OFF | 0.06 | 0.05 | 0.11 | 0.14
29 | OFF | OFF | 0.06 | 0.04 | 0.09 | 0.05 | 0.12
30 | OFF | OFF | OFF | 0.03 | 0.04 | 0.04 | 0.1
31 | 0.06 | OFF | OFF | 0.05 | 0.04 | 0.09 | 0.13
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
[5 empty] | James Winge |  | April 1 2025
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Mar. 2025 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / |  | 1.29 | 120 | 154.8 | 8.9 | 7 | 26 | Y | 500
2 / |  | 1.28 | 120 | 153.6 | 9 | 7 | 26 | Y | 500
3 / |  | 1.32 | 120 | 158.4 | 9.4 | 6.9 | 26 | Y | 500
4 / |  | 1.29 | 120 | 154.8 | 9.4 | 7 | 26 | Y | 500
5 / |  | 1.33 | 120 | 159.6 | 9.3 | 7 | 26 | Y | 500
6 / |  | 1.22 | 120 | 146.4 | 8.6 | 7.1 | 31 | Y | 500
7 / |  | 1.3 | 120 | 156 | 8.8 | 7 | 26 | Y | 500
8 / |  | 1.29 | 120 | 154.8 | 8.7 | 7 | 26 | Y | 500
9 / |  | 1.29 | 120 | 154.8 | 8.8 | 7 | 26 | Y | 500
10/ |  | 1.3 | 120 | 156 | 9.1 | 7 | 26 | Y | 500
11/ |  | 1.25 | 120 | 150 | 9 | 7.2 | 31 | Y | 500
12/ |  | 1.25 | 120 | 150 | 9.1 | 7.2 | 31 | Y | 500
13/ |  | 1.25 | 120 | 150 | 9 | 7.2 | 31 | Y | 500
14/ |  | 1.18 | 120 | 141.6 | 8.6 | 7.1 | 31 | Y | 500
15/ |  | 1.21 | 120 | 145.2 | 8.2 | 7.2 | 31 | Y | 500
16/ |  | 1.29 | 120 | 154.8 | 8.4 | 7.1 | 31 | Y | 500
17/ |  | 1.18 | 120 | 141.6 | 8.4 | 7 | 25 | Y | 500
18/ |  | 1.31 | 120 | 157.2 | 8.6 | 7 | 26 | Y | 500
19/ |  | 1.32 | 120 | 158.4 | 9 | 7 | 26 | Y | 500
20/ |  | 1.32 | 120 | 158.4 | 9 | 7.1 | 31 | Y | 500
21/ |  | 1.3 | 120 | 156 | 9.3 | 7 | 26 | Y | 500
22/ |  | 1.28 | 120 | 153.6 | 9.1 | 7 | 26 | Y | 500
23/ |  | 1.34 | 120 | 160.8 | 9.3 | 7 | 26 | Y | 500
24/ |  | 1.28 | 120 | 153.6 | 9.8 | 7 | 26 | Y | 500
25/ |  | 1.33 | 120 | 159.6 | 10.5 | 7 | 19 | Y | 500
26/ |  | 1.34 | 120 | 160.8 | 11.3 | 7 | 19 | Y | 500
27/ |  | 1.29 | 120 | 154.8 | 11.7 | 7 | 19 | Y | 500
28/ |  | 1.33 | 120 | 159.6 | 11.1 | 7 | 19 | Y | 500
29/ |  | 1.16 | 120 | 139.2 | 10.7 | 7 | 19 | Y | 500
30/ |  | 1.27 | 120 | 152.4 | 10.4 | 7 | 19 | Y | 500
31/ |  | 1.3 | 120 | 156 | 10 | 7 | 19 | Y | 500
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2