## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2025-04-01
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.05 | OFF | 0.05 | 0.04 | 0.05 | 0.05 | 0.1
2 | 0.04 | OFF | 0.04 | 0.05 | 0.04 | 0.04 | 0.1
3 | 0.06 | OFF | OFF | OFF | 0.04 | 0.08 | 0.1
4 | 0.03 | OFF | 0.04 | 0.04 | 0.06 | 0.05 | 0.1
5 | 0.03 | 0.03 | OFF | OFF | 0.06 | 0.04 | 0.11
6 | 0.07 | OFF | OFF | 0.04 | 0.04 | 0.1 | 0.1
7 | 0.06 | 0.05 | OFF | 0.04 | 0.06 | 0.05 | 0.12
8 | 0.04 | OFF | OFF | 0.06 | 0.06 | OFF | 0.28
9 | 0.13 | OFF | OFF | 0.08 | OFF | 0.04 | 0.22
10 | 0.06 | OFF | 0.05 | 0.05 | OFF | 0.04 | 0.14
11 | 0.06 | OFF | OFF | 0.05 | OFF | 0.04 | 0.12
12 | 0.08 | OFF | OFF | 0.06 | 0.05 | OFF | 0.13
13 | 0.1 | OFF | OFF | 0.06 | 0.04 | OFF | 0.21
14 | 0.06 | OFF | OFF | 0.12 | OFF | 0.04 | 0.2
15 | 0.06 | OFF | OFF | 0.04 | 0.08 | OFF | 0.12
16 | 0.04 | OFF | 0.04 | 0.04 | 0.05 | OFF | 0.1
17 | 0.04 | OFF | 0.04 | 0.05 | 0.05 | OFF | 0.12
18 | 0.04 | OFF | 0.04 | 0.06 | 0.04 | OFF | 0.12
19 | 0.04 | 0.06 | OFF | 0.04 | OFF | 0.04 | 0.1
20 | 0.05 | OFF | 0.05 | 0.04 | OFF | 0.04 | 0.11
21 | 0.05 | OFF | 0.04 | 0.12 | 0.07 | OFF | 0.12
22 | 0.05 | OFF | 0.05 | 0.05 | 0.05 | OFF | 0.11
23 | 0.05 | OFF | 0.04 | 0.05 | 0.04 | 0.04 | 0.12
24 | 0.05 | OFF | 0.05 | 0.04 | 0.05 | 0.05 | 0.07
25 | 0.07 | 0.05 | 0.05 | OFF | 0.05 | 0.05 | 0.09
26 | OFF | OFF | 0.04 | 0.08 | 0.04 | 0.04 | 0.1
27 | OFF | 0.05 | OFF | 0.04 | 0.05 | 0.04 | 0.1
28 | 0.05 | OFF | 0.05 | 0.06 | 0.06 | OFF | 0.1
29 | 0.05 | OFF | 0.05 | 0.04 | 0.05 | OFF | 0.13
30 | 0.08 | OFF | 0.07 | 0.06 | 0.05 | OFF | 0.1
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
[5 empty] | James Winge |  | 2025-05-01
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2025-04-01 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.28 | 120 | 153.6 | 10.2 | 7.2 | 23 | Y | 500
2 / | 8:00 | 1.27 | 120 | 152.4 | 10.2 | 7 | 19 | Y | 500
3 / | 8:00 | 1.23 | 120 | 147.6 | 10.1 | 7.2 | 23 | Y | 500
4 / | 8:00 | 1.33 | 120 | 159.6 | 10 | 7.1 | 23 | Y | 500
5 / | 8:00 | 1.31 | 120 | 157.2 | 10.4 | 7 | 19 | Y | 500
6 / | 8:00 | 1.26 | 120 | 151.2 | 10.8 | 6.9 | 19 | Y | 500
7 / | 8:00 | 1.25 | 120 | 150 | 10.6 | 7 | 19 | Y | 500
8 / | 8:00 | 1.21 | 96.7742 | 117.0968 | 11 | 6.9 | 19 | Y | 620
9 / | 8:00 | 1.22 | 96.7742 | 118.0645 | 11 | 6.8 | 19 | Y | 620
10/ | 8:00 | 1.15 | 96.7742 | 111.2903 | 10.8 | 6.9 | 19 | Y | 620
11/ | 8:00 | 1.19 | 96.7742 | 115.1613 | 11.1 | 7.1 | 23 | Y | 620
12/ | 8:00 | 1.27 | 96.7742 | 122.9032 | 11 | 7 | 19 | Y | 620
13/ | 8:00 | 1.24 | 96.7742 | 120 | 10.7 | 7 | 19 | Y | 620
14/ | 8:00 | 1.24 | 96.7742 | 120 | 10.9 | 6.9 | 19 | Y | 620
15/ | 8:00 | 1.21 | 96.7742 | 117.0968 | 11.4 | 6.9 | 19 | Y | 620
16/ | 8:00 | 1.2 | 96.7742 | 116.129 | 12 | 7 | 19 | Y | 620
17/ | 8:00 | 1.19 | 96.7742 | 115.1613 | 12 | 7 | 19 | Y | 620
18/ | 8:00 | 1.24 | 96.7742 | 120 | 12 | 7 | 19 | Y | 620
19/ | 8:00 | 1.23 | 96.7742 | 119.0323 | 12 | 7 | 19 | Y | 620
20/ | 8:00 | 1.19 | 96.7742 | 115.1613 | 12.2 | 6.8 | 19 | Y | 620
21/ | 8:00 | 1.23 | 96.7742 | 119.0323 | 11.4 | 7 | 19 | Y | 620
22/ | 8:00 | 1.24 | 96.7742 | 120 | 11.6 | 7 | 19 | Y | 620
23/ | 8:00 | 1.19 | 96.7742 | 115.1613 | 11.7 | 7 | 19 | Y | 620
24/ | 8:00 | 1.18 | 96.7742 | 114.1935 | 12 | 7 | 19 | Y | 620
25/ | 8:00 | 1.19 | 96.7742 | 115.1613 | 12 | 7 | 19 | Y | 620
26/ | 8:00 | 1.15 | 96.7742 | 111.2903 | 12.5 | 7 | 19 | Y | 620
27/ | 8:00 | 1.2 | 96.7742 | 116.129 | 12.4 | 7 | 19 | Y | 620
28/ | 8:00 | 1.22 | 96.7742 | 118.0645 | 12.4 | 7.1 | 23 | Y | 620
29/ | 8:00 | 1.19 | 96.7742 | 115.1613 | 12.6 | 7 | 19 | Y | 620
30/ | 8:00 | 1.09 | 96.7742 | 105.4839 | 12.7 | 7 | 19 | Y | 620
31/ |  |  | #DIV/0! | #DIV/0!
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2