## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | 2025-05-01
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.06 | 0.05 | 0.05 | 0.05 | 0.06 | OFF | 0.08
2 | 0.05 | OFF | 0.05 | 0.06 | 0.05 | 0.04 | 0.08
3 | 0.05 | 0.06 | OFF | 0.05 | 0.05 | 0.06 | 0.08
4 | 0.04 | OFF | 0.05 | 0.04 | 0.05 | 0.05 | 0.09
5 | 0.05 | OFF | 0.06 | 0.05 | 0.04 | 0.06 | 0.08
6 | 0.07 | OFF | 0.04 | 0.06 | 0.04 | 0.04 | 0.08
7 | 0.06 | 0.05 | 0.05 | 0.05 | 0.05 | 0.04 | 0.09
8 | 0.05 | OFF | 0.06 | 0.05 | 0.04 | 0.1 | 0.1
9 | 0.05 | OFF | 0.05 | 0.06 | 0.04 | 0.05 | 0.1
10 | 0.05 | 0.04 | 0.04 | 0.05 | 0.05 | 0.04 | 0.09
11 | OFF | 0.05 | 0.05 | OFF | 0.04 | OFF | 0.09
12 | 0.06 | OFF | 0.06 | 0.05 | 0.08 | 0.06 | 0.12
13 | OFF | 0.05 | 0.07 | 0.07 | 0.05 | 0.04 | 0.11
14 | 0.06 | OFF | 0.05 | 0.05 | 0.08 | 0.05 | 0.1
15 | 0.08 | OFF | 0.06 | 0.06 | 0.05 | 0.05 | 0.1
16 | 0.05 | OFF | 0.05 | 0.06 | 0.06 | 0.06 | 0.11
17 | 0.05 | OFF | 0.06 | 0.05 | OFF | 0.06 | 0.11
18 | 0.06 | OFF | 0.05 | 0.05 | 0.08 | 0.06 | 0.11
19 | OFF | 0.07 | 0.09 | 0.06 | 0.14 | 0.1 | 0.14
20 | 0.06 | OFF | 0.06 | 0.05 | 0.06 | 0.06 | 0.13
21 | 0.08 | OFF | 0.06 | 0.06 | 0.05 | 0.06 | 0.13
22 | 0.07 | OFF | 0.11 | 0.06 | OFF | 0.06 | 0.14
23 | 0.08 | OFF | 0.06 | 0.06 | 0.06 | 0.06 | 0.12
24 | 0.06 | 0.06 | OFF | 0.06 | 0.06 | 0.06 | 0.11
25 | 0.06 | OFF | 0.06 | 0.06 | 0.07 | 0.06 | 0.1
26 | 0.06 | 0.06 | 0.06 | 0.07 | 0.06 | 0.06 | 0.11
27 | 0.07 | OFF | 0.08 | 0.08 | 0.08 | 0.08 | 0.12
28 | 0.08 | 0.09 | 0.08 | 0.06 | 0.05 | 0.06 | 0.11
29 | 0.07 | OFF | 0.06 | 0.06 | 0.06 | 0.06 | 0.12
30 | 0.06 | OFF | 0.1 | 0.06 | 0.06 | 0.05 | 0.14
31 | 0.05 | OFF | 0.05 | 0.05 | 0.05 | 0.05 | 0.09
Conventional or Direct Filtration
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
[5 empty] | James Winge |  | 2025-06-04
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | 2025-05-01 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.12 | 96.7742 | 108.3871 | 12.7 | 7 | 19 | YES | 620
2 / | 8:00 | 1.13 | 96.7742 | 109.3548 | 13.4 | 7 | 19 | YES | 620
3 / | 8:00 | 1.16 | 96.7742 | 112.2581 | 13.1 | 7 | 19 | YES | 620
4 / | 8:00 | 1.1 | 96.7742 | 106.4516 | 13 | 7.1 | 23 | YES | 620
5 / | 8:00 | 1.11 | 96.7742 | 107.4194 | 12.7 | 7 | 19 | YES | 620
6 / | 8:00 | 1.13 | 96.7742 | 109.3548 | 13 | 7 | 19 | YES | 620
7 / | 8:00 | 1.16 | 96.7742 | 112.2581 | 14 | 7 | 19 | YES | 620
8 / | 8:00 | 1.11 | 96.7742 | 107.4194 | 13.6 | 7.2 | 23 | YES | 620
9 / | 8:00 | 1.17 | 96.7742 | 113.2258 | 13.4 | 7.1 | 23 | YES | 620
10/ | 8:00 | 1.18 | 96.7742 | 114.1935 | 14 | 7.1 | 23 | YES | 620
11/ | 8:00 | 1.13 | 96.7742 | 109.3548 | 13.6 | 7 | 19 | YES | 620
12/ | 8:00 | 1.22 | 96.7742 | 118.0645 | 12.6 | 7.1 | 23 | YES | 620
13/ | 8:00 | 1.13 | 96.7742 | 109.3548 | 13 | 7.2 | 23 | YES | 620
14/ | 8:00 | 1.16 | 96.7742 | 112.2581 | 13 | 7 | 19 | YES | 620
15/ | 8:00 | 1.14 | 96.7742 | 110.3226 | 13.1 | 7.1 | 23 | YES | 620
16/ | 8:00 | 1.21 | 96.7742 | 117.0968 | 12.1 | 7.1 | 23 | YES | 620
17/ | 8:00 | 1.12 | 96.7742 | 108.3871 | 12.9 | 7 | 19 | YES | 620
18/ | 8:00 | 1.16 | 96.7742 | 112.2581 | 13 | 7 | 19 | YES | 620
19/ | 8:00 | 1.17 | 96.7742 | 113.2258 | 12.5 | 7.2 | 23 | YES | 620
20/ | 8:00 | 1.14 | 96.7742 | 110.3226 | 13.6 | 7.1 | 23 | YES | 620
21/ | 8:00 | 1.12 | 96.7742 | 108.3871 | 13 | 7.1 | 23 | YES | 620
22/ | 8:00 | 1.1 | 96.7742 | 106.4516 | 13.4 | 7 | 19 | YES | 620
23/ | 8:00 | 1.14 | 96.7742 | 110.3226 | 13 | 7 | 19 | YES | 620
24/ | 8:00 | 1.1 | 96.7742 | 106.4516 | 13.7 | 7.1 | 23 | YES | 620
25/ | 8:00 | 1.17 | 96.7742 | 113.2258 | 13.9 | 7 | 19 | YES | 620
26/ | 8:00 | 1.16 | 96.7742 | 112.2581 | 14 | 7.1 | 23 | YES | 620
27/ | 8:00 | 1.18 | 96.7742 | 114.1935 | 14.5 | 7.1 | 23 | YES | 620
28/ | 8:00 | 1.1 | 96.7742 | 106.4516 | 15.5 | 7.1 | 15 | YES | 620
29/ | 8:00 | 1 | 96.7742 | 96.7742 | 16.4 | 7.1 | 15 | YES | 620
30/ | 8:00 | 1.13 | 96.7742 | 109.3548 | 15.7 | 7.1 | 15 | YES | 620
31/ | 8:00 | 1.2 | 96.7742 | 116.129 | 16 | 6.9 | 13 | YES | 620
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2