## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Jun.2025
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.05 | OFF | 0.05 | 0.05 | 0.07 | 0.05 | 0.09
2 | 0.06 | OFF | 0.05 | 0.09 | 0.05 | 0.05 | 0.09
3 | 0.07 | 0.05 | 0.05 | 0.07 | 0.05 | 0.05 | 0.09
4 | 0.07 | 0.08 | 0.08 | 0.05 | 0.1 | 0.06 | 0.14
5 | 0.06 | OFF | 0.11 | 0.05 | OFF | 0.06 | 0.11
6 | 0.08 | OFF | 0.06 | 0.06 | 0.07 | 0.1 | 0.12
7 | 0.07 | 0.07 | 0.07 | 0.06 | 0.06 | 0.06 | 0.12
8 | 0.06 | OFF | 0.08 | 0.07 | 0.07 | 0.09 | 0.12
9 | 0.08 | OFF | 0.08 | 0.08 | 0.08 | 0.07 | 0.12
10 | 0.08 | OFF | 0.07 | 0.07 | 0.08 | 0.12 | 0.12
11 | 0.12 | OFF | 0.08 | 0.07 | OFF | 0.08 | 0.11
12 | 0.13 | OFF | 0.08 | 0.12 | 0.06 | 0.06 | 0.13
13 | 0.08 | 0.09 | 0.12 | 0.06 | OFF | 0.06 | 0.12
14 | OFF | 0.06 | 0.06 | 0.05 | 0.06 | 0.1 | 0.11
15 | 0.05 | 0.06 | 0.07 | 0.09 | 0.05 | 0.06 | 0.12
16 | 0.07 | OFF | 0.06 | 0.06 | 0.07 | OFF | 0.12
17 | 0.08 | OFF | 0.1 | 0.06 | 0.06 | 0.08 | 0.12
18 | OFF | OFF | 0.07 | 0.08 | 0.06 | 0.07 | 0.12
19 | 0.09 | OFF | 0.07 | 0.08 | 0.08 | 0.08 | 0.11
20 | OFF | 0.08 | 0.08 | OFF | 0.07 | OFF | 0.16
21 | 0.1 | 0.12 | 0.12 | 0.09 | 0.08 | OFF | 0.18
22 | 0.09 | OFF | 0.14 | OFF | 0.08 | OFF | 0.14
23 | 0.07 | OFF | 0.09 | 0.07 | 0.08 | 0.09 | 0.14
24 | 0.8 | OFF | 0.1 | 0.07 | 0.07 | 0.08 | 0.16
25 | 0.08 | 0.08 | 0.08 | 0.12 | 0.08 | 0.08 | 0.12
26 | 0.09 | OFF | 0.1 | 0.08 | 0.1 | 0.8 | 0.12
27 | 0.1 | 0.08 | 0.09 | 0.08 | 0.08 | 0.08 | 0.16
28 | 0.09 | 0.08 | 0.08 | 0.09 | 0.09 | 0.09 | 0.15
29 | 0.09 | OFF | 0.09 | 0.11 | 0.09 | 0.09 | 0.15
30 | 0.1 | 0.1 | 0.09 | 0.07 | 0.08 | 0.08 | 0.14
31
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:July 1 2025
James Winge
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Jun.2025 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.21 | 96.7742 | 117.0968 | 16 | 7 | 13 | YES | 620
2 / | 8:00 | 1.21 | 96.7742 | 117.0968 | 15.9 | 7 | 13 | YES | 620
3 / | 8:00 | 1.26 | 96.7742 | 121.9355 | 15.7 | 7 | 13 | YES | 620
4 / | 8:00 | 1.23 | 96.7742 | 119.0323 | 15.9 | 7 | 13 | YES | 620
5 / | 8:00 | 1.15 | 81.9672 | 94.2623 | 16.3 | 7.1 | 31 | YES | 732
6 / | 8:00 | 1.24 | 81.9672 | 101.6393 | 17.5 | 7 | 26 | YES | 732
7 / | 8:00 | 1.12 | 81.9672 | 91.8033 | 18.3 | 7 | 25 | YES | 732
8 / | 8:00 | 1.1 | 81.9672 | 90.1639 | 19 | 7 | 25 | YES | 732
9 / | 8:00 | 1.08 | 81.9672 | 88.5246 | 19.3 | 7 | 25 | YES | 732
10/ | 8:00 | 1.05 | 81.9672 | 86.0656 | 19.6 | 6.9 | 25 | YES | 732
11/ | 8:00 | 1.15 | 81.9672 | 94.2623 | 18.4 | 7 | 25 | YES | 732
12/ | 8:00 | 1.28 | 81.9672 | 104.918 | 17.6 | 7.1 | 31 | YES | 732
13/ | 8:00 | 1.2 | 81.9672 | 98.3607 | 16.9 | 7 | 25 | YES | 732
14/ | 8:00 | 1.27 | 81.9672 | 104.0984 | 15.9 | 7 | 26 | YES | 732
15/ | 8:00 | 1.25 | 81.9672 | 102.459 | 15.4 | 7 | 26 | YES | 732
16/ | 8:00 | 1.32 | 81.9672 | 108.1967 | 16.6 | 7.1 | 31 | YES | 732
17/ | 8:00 | 1.27 | 81.9672 | 104.0984 | 16.4 | 7 | 26 | YES | 732
18/ | 8:00 | 1.13 | 81.9672 | 92.623 | 17.2 | 7 | 25 | YES | 732
19/ | 8:00 | 1.25 | 81.9672 | 102.459 | 17 | 7 | 26 | YES | 732
20/ | 8:00 | 1.24 | 81.9672 | 101.6393 | 16.4 | 7 | 26 | YES | 732
21/ | 8:00 | 1.26 | 81.9672 | 103.2787 | 15.5 | 7 | 26 | YES | 732
22/ | 8:00 | 1.22 | 81.9672 | 100 | 14 | 7 | 39 | YES | 732
23/ | 8:00 | 1.2 | 81.9672 | 98.3607 | 15.5 | 7 | 26 | YES | 732
24/ | 8:00 | 1.19 | 81.9672 | 97.541 | 17 | 7.1 | 31 | YES | 732
25/ | 8:00 | 1.23 | 81.9672 | 100.8197 | 17.4 | 7 | 26 | YES | 732
26/ | 8:00 | 1.19 | 81.9672 | 97.541 | 17.5 | 7.1 | 31 | YES | 732
27/ | 8:00 | 1.19 | 81.9672 | 97.541 | 17.1 | 7 | 25 | YES | 732
28/ | 8:00 | 1.14 | 81.9672 | 93.4426 | 17.6 | 7 | 25 | YES | 732
29/ | 8:00 | 1.18 | 81.9672 | 96.7213 | 18.5 | 6.9 | 25 | YES | 732
30/ | 8:00 | 1.12 | 81.9672 | 91.8033 | 19.8 | 7.1 | 31 | YES | 732
31/ |  |  | #DIV/0! | #DIV/0!
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2