## Sheet1
OHA - Drinking Water Program - Turbidity Monitoring Report Form | [6 empty] | County: Benton
Conventional or Direct Filtration
System Name: | Philomath Public Works |  |  | ID #: OR41-00624-A |  | Month/Year | Jul. 2025
Day | 0:00 | 4:00 | 8:00 | NOON | 16:00 | 20:00 | Highest Reading
| (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | (NTU) | of the Day¹ (NTU)
1 | 0.07 | 0.12 | 0.08 | 0.07 | 0.08 | 0.08 | 0.14
2 | 0.09 | OFF | 0.1 | 0.09 | 0.1 | 0.1 | 0.14
3 | 0.13 | OFF | 0.1 | 0.07 | 0.08 | 0.08 | 0.17
4 | 0.08 | 0.08 | 0.09 | 0.09 | 0.12 | 0.11 | 0.12
5 | 0.09 | OFF | 0.1 | 0.08 | 0.07 | 0.07 | 0.11
6 | 0.09 | OFF | 0.08 | 0.07 | 0.1 | 0.07 | 0.12
7 | 0.08 | OFF | 0.08 | 0.08 | 0.14 | 0.08 | 0.14
8 | 0.1 | OFF | 0.09 | 0.08 | 0.08 | 0.08 | 0.12
9 | 0.08 | OFF | 0.09 | 0.09 | 0.09 | 0.09 | 0.15
10 | 0.1 | OFF | 0.12 | 0.09 | 0.07 | 0.12 | 0.12
11 | 0.07 | OFF | 0.07 | 0.08 | 0.08 | 0.08 | 0.14
12 | 0.1 | 0.01 | OFF | 0.07 | 0.08 | 0.11 | 0.16
13 | 0.09 | OFF | 0.08 | 0.07 | 0.08 | 0.08 | 0.15
14 | 0.08 | 0.08 | 0.09 | 0.08 | 0.11 | 0.09 | 0.15
15 | 0.11 | OFF | 0.14 | 0.07 | 0.07 | 0.08 | 0.18
16 | 0.09 | OFF | 0.08 | 0.07 | 0.14 | 0.1 | 0.14
17 | 0.14 | OFF | 0.16 | 0.07 | 0.1 | 0.1 | 0.16
18 | 0.08 | OFF | 0.1 | 0.12 | 0.08 | 0.09 | 0.18
19 | 0.07 | OFF | 0.07 | 0.08 | 0.08 | 0.1 | 0.15
20 | 0.09 | OFF | 0.09 | 0.09 | 0.07 | 0.09 | 0.15
21 | 0.14 | 0.1 | 0.07 | 0.08 | 0.08 | 0.08 | 0.16
22 | 0.1 | OFF | 0.1 | 0.1 | 0.1 | 0.12 | 0.18
23 | 0.14 | OFF | 0.11 | 0.08 | 0.08 | 0.08 | 0.18
24 | 0.09 | 0.08 | 0.08 | 0.09 | 0.1 | 0.09 | 0.14
25 | 0.09 | 0.08 | 0.08 | 0.08 | 0.09 | OFF | 0.15
26 | 0.09 | 0.08 | 0.17 | 0.09 | OFF | OFF | 0.17
27 | 0.11 | 0.1 | 0.11 | 0.11 | OFF | 0.14 | 0.17
28 | 0.18 | OFF | 0.16 | 0.09 | 0.1 | 0.15 | 0.18
29 | 0.1 | OFF | 0.1 | 0.08 | OFF | 0.14 | 0.16
30 | 0.09 | 0.09 | 0.08 | 0.08 | OFF | 0.09 | 0.16
31 | 0.1 | 0.1 | 0.09 | 0.08 | 0.07 | OFF | 0.15
Conventional or Direct Filtration |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of the 4-hour turbidity readings ≤ 0.3 NTU? |  |  | YES | CT's met everyday? |  | All Cl2 residual at entry point ≥ 0.2 mg/L ?
All the 4-hour turbidity readings ≤ 1 NTU? |  |  | YES | (see back) |  | YES
All turbidity readings < IFE² triggers? |  |  | YES | YES
Notes: |  |  |  | PRINTED NAME: |  | James Winge T-08175
|  |  |  | SIGNATURE: |  |  | DATE:
[5 empty] | James Winge |  | 2025-08-01
PHONE #
|  |  |  | 1-541-929-3579 | 541-609-9008
¹ Including continuous turbidity data, if applicable, for optimization recording purposes. Compliance values in columns "12 AM" through
"8 PM" my not corrospond to continuous readings' maximum. |  |  |  |  | ² IFE = Individ. Filter Effl. (OAR 333-061-0040(1)(e)(B&C))
PAGE 1 of 2

## Sheet2
Oregon DHS - Drinking Water Program - Surface Water Quality Data Form
Required Log < 700 gpm = 0.5
Philomath Public Works ID #: OR41-00624-A |  |  |  |  | DATE | Jul. 2025 | Required Log > 700 gpm = 1.0
|  | Minimum Cl₂ | Contact | Actual |  |  | Required |  | Peak Hourly
Date | / Time | Residual at | Time | CT | Temp | pH | CT | CT Met? | Demand
|  | 1st User ( C )³ | ( T ) | [5 empty] | Flow
|  | ppm or mg/L | minutes | C X T | °C |  | Use Tables | YES / NO | GPM
1 / | 8:00 | 1.06 | 82.1918 | 87.1233 | 20.2 | 7 | 19 | Y | 730
2 / | 8:00 | 1 | 82.1918 | 82.1918 | 20.1 | 7.1 | 22 | Y | 730
3 / | 8:00 | 1.17 | 82.1918 | 96.1644 | 20.2 | 7.1 | 23 | Y | 730
4 / | 8:00 | 1.2 | 82.1918 | 98.6301 | 19.6 | 7.1 | 31 | Y | 730
5 / | 8:00 | 1.21 | 82.1918 | 99.4521 | 18.6 | 7 | 25 | Y | 730
6 / | 8:00 | 1.28 | 82.1918 | 105.2055 | 19.1 | 7 | 26 | Y | 730
7 / | 8:00 | 1.21 | 82.1918 | 99.4521 | 19.7 | 7.1 | 31 | Y | 730
8 / | 8:00 | 1.09 | 82.1918 | 89.589 | 20.8 | 6.9 | 19 | Y | 730
9 / | 8:00 | 1.19 | 82.1918 | 97.8082 | 20.3 | 7.2 | 23 | Y | 730
10/ | 8:00 | 1.1 | 82.1918 | 90.411 | 20.8 | 7 | 19 | Y | 730
11/ | 8:00 | 1.2 | 82.1918 | 98.6301 | 20.4 | 7 | 19 | Y | 730
12/ | 8:00 | 1.17 | 82.1918 | 96.1644 | 21 | 7 | 19 | Y | 730
13/ | 8:00 | 1.2 | 82.1918 | 98.6301 | 21.4 | 7 | 19 | Y | 730
14/ | 8:00 | 1.06 | 82.1918 | 87.1233 | 22.6 | 7 | 19 | Y | 730
15/ | 8:00 | 1.03 | 71.4286 | 73.5714 | 21.7 | 7 | 19 | Y | 840
16/ | 8:00 | 1.08 | 71.4286 | 77.1429 | 21.7 | 7 | 19 | Y | 840
17/ | 8:00 | 1.14 | 71.4286 | 81.4286 | 21.5 | 7 | 19 | Y | 840
18/ | 8:00 | 1.08 | 71.4286 | 77.1429 | 20.7 | 7 | 19 | Y | 840
19/ | 8:00 | 1.19 | 71.4286 | 85 | 20.4 | 7 | 19 | Y | 840
20/ | 8:00 | 1.2 | 71.4286 | 85.7143 | 20.5 | 6.9 | 19 | Y | 840
21/ | 8:00 | 1.25 | 71.4286 | 89.2857 | 19.4 | 6.9 | 19 | Y | 840
22/ | 8:00 | 1.28 | 71.4286 | 91.4286 | 19 | 7 | 26 | Y | 840
23/ | 8:00 | 1.24 | 71.4286 | 88.5714 | 19.9 | 7 | 26 | Y | 840
24/ | 8:00 | 1.25 | 71.4286 | 89.2857 | 20.1 | 7.2 | 23 | Y | 840
25/ | 8:00 | 1.24 | 71.4286 | 88.5714 | 19.78 | 7.1 | 31 | Y | 840
26/ | 8:00 | 1.1 | 71.4286 | 78.5714 | 20.2 | 7.2 | 23 | Y | 840
27/ | 8:00 | 1.13 | 71.4286 | 80.7143 | 19.3 | 7.1 | 31 | Y | 840
28/ | 8:00 | 1.18 | 71.4286 | 84.2857 | 19.4 | 7.2 | 31 | Y | 840
29/ | 8:00 | 1.1 | 71.4286 | 78.5714 | 20 | 7.1 | 23 | Y | 840
30/ | 8:00 | 1.11 | 71.4286 | 79.2857 | 20.2 | 7.2 | 23 | Y | 840
31/ | 8:00 | 1 | 71.4286 | 71.4286 | 20.6 | 7.3 | 22 | Y | 840
³ If CL₂ at entry point < 0.2 mg/L, or CT not met, notify DWP by end of next business day.
PAGE 2 of 2