## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-07-01
System Name: | Seal Rock Water District |  |  | 41-00798 |  |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | 0.05 | 0.03 | 0.03 | OFF | 0.05
2 | OFF | OFF | 0.04 | 0.03 | 0.02 | OFF | 0.04
3 | OFF | OFF | OFF | OFF | 0.04 | OFF | 0.04
4 | OFF | OFF | OFF | OFF | 0.04 | OFF | OFF
5 | OFF | OFF | 0.08 | 0.03 | 0.02 | OFF | 0.08
6 | OFF | OFF | 0.01 | 0.01 | 0.03 | OFF | 0.03
7 | OFF | OFF | 0.03 | 0.01 | 0.03 | OFF | 0.03
8 | OFF | OFF | 0.04 | 0.03 | 0.03 | OFF | 0.04
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | 0.05 | 0.03 | 0.03 | OFF | OFF | 0.05
12 | OFF | OFF | 0.03 | 0.01 | 0.03 | OFF | 0.03
13 | OFF | OFF | 0.04 | 0.03 | 0.04 | OFF | 0.04
14 | OFF | OFF | 0.04 | 0.035 | 0.04 | OFF | 0.04
15 | OFF | OFF | 0.05 | 0.08 | 0.03 | OFF | 0.08
16 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
17 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
18 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
19 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
20 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
21 | OFF | OFF | OFF | 0.01 | 0.02 | OFF | 0.02
22 | OFF | OFF | 0.02 | 0.03 | 0.03 | OFF | 0.03
23 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
26 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
27 | OFF | OFF | 0.04 | 0.03 | 0.03 | OFF | 0.04
28 | OFF | OFF | 0.04 | 0.03 | 0.04 | OFF | 0.04
29 | OFF | OFF | 0.03 | 0.03 | 0.04 | OFF | 0.04
30 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
31 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME:Larry Estes
[5 empty] | SIGNATURE:Larry Estes |  |  | DATE:08-02-2022
[5 empty] | PHONE #: ( 541 ) 563-7715 |  |  | CERT #:T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: SealRock Water District |  |  | ID#: 41 -00798 |  | Month/Year: | 2022-07-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 0.67 | 47.47 | 31.8049 | 16.55 | 7.27 | 13.07 | YES
2 | [7 empty] | Closed
3 | 0.68 | 25.97 | 17.6596 | 16.5 | 7.38 | 13.6772 | YES
4 | 0.68 | 20.13 | 13.6884 | 16.7 | 7.2 | 12.6206 | YES
5 | 0.91 | 35.67 | 32.4597 | 16.7 | 7.33 | 13.5997 | YES
6 | 0.91 | 43.27 | 39.3757 | 16.7 | 7.08 | 12.3909 | YES
7 | 0.85 | 62.76 | 53.346 | 16.7 | 7.1 | 12.398 | YES
8 | 0.72 | 71.38 | 51.3936 | 16.8 | 7.1 | 12.1328 | YES
9 | [7 empty] | Closed
10 | [7 empty] | Closed
11 | 0.95 | 22.48 | 21.356 | 17.9 | 7.1 | 11.5693 | YES
12 | 0.87 | 62.19 | 54.1053 | 18.4 | 7.1 | 11.0838 | YES
13 | 0.75 | 92.31 | 69.2325 | 18.2 | 7.2 | 11.5025 | YES
14 | 0.78 | 55.51 | 43.2978 | 18 | 7 | 10.8553 | YES
15 | 0.75 | 52.88 | 39.66 | 18 | 7.1 | 11.2305 | YES
16 | [7 empty] | Closed
17 | [7 empty] | Closed
18 | 0.79 | 54.51 | 43.0629 | 17.8 | 7.3 | 12.3219 | YES
19 | 1.04 | 41.49 | 43.1496 | 17.8 | 7.2 | 12.2161 | YES
20 | 1.08 | 75.54 | 81.5832 | 18.16 | 7.26 | 12.2502 | YES
21 | 1.04 | 38.63 | 40.1752 | 18.039 | 7.24 | 12.2023 | YES
22 | 1.32 | 58.32 | 76.9824 | 16.6 | 7.2 | 13.671 | YES
23 | [7 empty] | Closed
24 | [7 empty] | Closed
25 | 1.21 | 30.86 | 37.3406 | 18.5 | 7.25 | 12.1082 | YES
26 | 1.45 | 48.12 | 69.774 | 18.5 | 7.27 | 12.5393 | YES
27 | 1.42 | 41.7 | 59.214 | 19 | 5.9 | 7.2097 | YES
28 | 1.29 | 38.7 | 49.923 | 19.4 | 5.61 | 6.1807 | YES
29 | 1.38 | 59.94 | 82.7172 | 19.8 | 7.05 | 10.4967 | YES
30 | [7 empty] | Closed
31 | [7 empty] | Closed
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2