## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-09-01
System Name: | Seal Rock Water District |  |  |  | ID# 41-00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | 0.05 | 0.06 | 0.03 | 0.05 | 0.06
2 | OFF | OFF | 0.04 | 0.05 | 0.05 | 0.02 | 0.05
3 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | OFF | OFF | 0.05 | 0.05 | 0.02 | OFF | 0.05
6 | OFF | OFF | 0.05 | 0.05 | 0.09 | 0.06 | 0.09
7 | OFF | OFF | 0.06 | 0.06 | 0.02 | 0.06 | 0.06
8 | OFF | 0.06 | 0.06 | 0.07 | 0.02 | 0.06 | 0.06
9 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
10 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
11 | OFF | OFF | 0.07 | 0.06 | 0.06 | off | 0.06
12 | OFF | OFF | 0.06 | 0.06 | 0.08 | OFF | 0.08
13 | OFF | OFF | 0.07 | 0.05 | 0.08 | OFF | 0.08
14 | OFF | OFF | 0.09 | 0.08 | 0.05 | OFF | 0.09
15 | OFF | OFF | 0.02 | 0.07 | 0.07 | 0.06 | 0.07
16 | OFF | OFF | 0.07 | OFF | OFF | OFF | 0.07
17 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
18 | OFF | OFF | OFF | OFF | OFF | 0.02 | 0.02
19 | OFF | 0.07 | 0.06 | 0.06 | 0.07 | 0.07 | 0.07
20 | OFF | 0.07 | 0.06 | 0.06 | 0.07 | 0.07 | 0.07
21 | OFF | 0.08 | 0.06 | 0.06 | 0.07 | OFF | 0.08
22 | OFF | 0.08 | 0.05 | 0.03 | 0.07 | OFF | 0.08
23 | OFF | OFF | 0.07 | 0.07 | 0.07 | OFF | 0.07
24 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
25 | OFF | OFF | OFF | OFF | OFF | 0.07 | 0.07
26 | OFF | 0.06 | 0.06 | 0.06 | 0.06 | OFF | 0.06
27 | OFF | OFF | 0.07 | 0.06 | 0.06 | OFF | 0.06
28 | OFF | OFF | 0.06 | 0.06 | 0.06 | OFF | 0.06
29 | OFF | OFF | 0.07 | 0.06 | 0.06 | OFF | 0.06
30 | OFF | OFF | 0.06 | 0.07 | 0.07 | OFF | 0.07
31 | OFF
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: September/2022 SealRock Water District |  |  |  |  | PRINTED NAME:Larry W Estes
[5 empty] | Larry W Estes |  |  | DATE:10-03-2022
[5 empty] | PHONE #: ( 541-563-7715 ) |  |  | CERT #:T-092229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : C
System Name: | Seal Rock Water Dist |  | 41-00798 |  | Month/Year: | 2022-09-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.05 | 64.67 | 67.9035 | 20.27 | 7.05 | 9.7882 | YES
2 | 1.2 | 59.94 | 71.928 | 20.2 | 6.31 | 7.5651 | YES
3 | 1.11 | 23.08 | 25.6188 | 19.8 | 7.01 | 10.023 | YES
4 | [7 empty] | off
5 | 1.14 | 54 | 61.56 | 19.4 | 6.54 | 8.6572 | YES
6 | 1.3 | 25.18 | 32.734 | 19.6 | 7.04 | 10.5023 | YES
7 | 1.15 | 34.04 | 39.146 | 19.1 | 6.36 | 8.2638 | YES
8 | 1.12 | 34 | 38.08 | 18.4 | 7.1 | 11.4072 | YES
9 | 1.05 | 18.5 | 19.425 | 18.3 | 6.8 | 10.181 | YES
10 | [7 empty] | off
11 | 1.17 | 33.12 | 38.7504 | 19.2 | 6.69 | 9.3192 | YES
12 | 1.43 | 18.88 | 26.9984 | 19.09 | 7 | 10.8699 | YES
13 | 1.2 | 24.64 | 29.568 | 19.14 | 7.29 | 11.7594 | YES
14 | 1.12 | 24.47 | 27.4064 | 19 | 7.42 | 12.3468 | YES
15 | 1.03 | 29.2 | 30.076 | 19.04 | 7.94 | 14.7881 | YES
16 | 0.96 | 34.45 | 33.072 | 18.7 | 7.79 | 14.1949 | YES
17 | [7 empty] | Off
18 | 1.06 | 24.97 | 26.4682 | 18.7 | 7.05 | 10.8962 | YES
19 | 1.08 | 43.84 | 47.3472 | 18.7 | 7.5 | 12.9197 | YES
20 | 1.25 | 37.43 | 46.7875 | 17.67 | 7.62 | 14.757 | YES
21 | 1.16 | 19.1 | 22.156 | 17.84 | 7 | 11.4633 | YES
22 | 1.14 | 51.31 | 58.4934 | 18.1 | 7.24 | 12.2926 | YES
23 | 0.97 | 51.43 | 49.8871 | 17.86 | 7.31 | 12.5751 | YES
24 | 1.07 | 23.94 | 25.6158 | 17.59 | 7.35 | 13.1468 | YES
25 | [7 empty] | off
26 | 0.73 | 24.83 | 18.1259 | 17.85 | 7.61 | 13.6889 | YES
27 | 1.22 | 47.29 | 57.6938 | 17.89 | 7.54 | 14.0678 | YES
28 | 1.22 | 19.91 | 24.2902 | 17.26 | 7.5 | 14.4567 | YES
29 | 1.22 | 63.4 | 77.348 | 17.19 | 7.2 | 12.9918 | YES
30 | 1.27 | 27.26 | 34.6202 | 17.2 | 7.2 | 13.0576 | YES
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2