## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2022-12-01
System Name: | SealRock Water District |  |  | ID#: | 41-00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | OFF | OFF | OFF | OFF | Plant off Buying water fromToledo
2 | OFF | OFF | OFF | OFF | OFF | OFF | Plant off Buying water fromToledo
3 | OFF | OFF | OFF | OFF | OFF | OFF | Plant off Buying water fromToledo
4 | OFF | OFF | OFF | OFF | OFF | OFF | Plant off Buying water fromToledo
5 | OFF | OFF | OFF | OFF | OFF | OFF | Plant off Buying water fromToledo
6 | OFF | OFF | 0.03 | 0.03 | 0.04 | OFF | 0.04
7 | OFF | OFF | 0.03 | 0.03 | OFF | OFF | 0.03
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
10 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | OFF | OFF | 0.02 | 0.02 | OFF | 0.02
13 | OFF | OFF | 0.04 | 0.02 | 0.03 | OFF | 0.04
14 | OFF | OFF | OFF | OFF | OFF | OFF | Off
15 | OFF | OFF | 0.04 | OFF | OFF | OFF | 0.04
16 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
17 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
18 | OFF | OFF | 0.02 | 0.03 | 0.02 | OFF | 0.03
19 | OFF | OFF | 0.03 | 0.02 | 0.07 | OFF | 0.07
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
22 | OFF | OFF | 0.03 | 0.02 | OFF | OFF | 0.03
23 | OFF | OFF | 0.03 | 0.02 | 0.09 | OFF | 0.09
24 | OFF | OFF | 0.03 | OFF | OFF | OFF | 0.03
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | OFF | OFF | Plant off Buying water from Newport
28 | OFF | OFF | OFF | 0.04 | 0.04 | 0.02 | 0.04
29 | OFF | OFF | 0.03 | 0.03 | 0.02 | OFF | 0.03
30 | OFF | OFF | 0.02 | 0.03 | OFF | OFF | 0.03
31 | OFF | OFF | 0.03 | 0.02 | OFF | OFF | 0.03
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME: Lary Estes
[5 empty] | SIGNATURE: |  |  | 2023-01-04
[5 empty] | PHONE #: ( 541 ) 563-7715 |  |  | CERT #:t-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: |  |  | ID#: 41 |  | Month/Year: |  | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | [7 empty] | off
2 | [7 empty] | off
3 | [7 empty] | off
4 | [7 empty] | off
5 | [7 empty] | off
6 | 1.02 | 39.28 | 40.0656 | 10.75 | 7.6 | 22.7072 | YES
7 | 0.96 | 68.67 | 65.9232 | 8.84 | 7.4 | 23.8524 | YES
8 | 1.11 | 62.9 | 69.819 | 9.95 | 7.2 | 21.0116 | YES
9 | [7 empty] | off
10 | 1.09 | 32.43 | 35.3487 | 8.76 | 7.34 | 23.8252 | YES
11 | [7 empty] | off
12 | 1.19 | 21.34 | 25.3946 | 9.13 | 6.51 | 17.6094 | YES
13 | 1.2 | 36.02 | 43.224 | 9.82 | 6.8 | 18.6281 | YES
14
15 | 1.15 | 36.07 | 41.4805 | 9.74 | 6.9 | 19.2759 | YES
16 | [7 empty] | off
17 | 1.05 | 32.75 | 34.3875 | 9.87 | 6.2 | 14.9019 | YES
18 | 1.31 | 66.57 | 87.2067 | 8.02 | 6.36 | 18.2042 | YES
19 | 1.23 | 34.75 | 42.7425 | 8.49 | 5.6 | 13.5686 | YES
20 | 1.32 | 25.87 | 34.1484 | 8.95 | 6.2 | 16.2592 | YES
21 | [7 empty] | off
22 | 1.1 | 102.61 | 112.871 | 10 | 6.67 | 17.4167 | YES
23 | 1.28 | 40.04 | 51.2512 | 10.1 | 7.5 | 23.5699 | YES
24 | 1.04 | 60 | 62.4 | 10.3 | 6.8 | 17.744 | YES
25 | [7 empty] | off
26 | [7 empty] | off
27 | [7 empty] | Newport Water Bought
28 | 1.2 | 59 | 70.8 | 11.9 | 6.97 | 17.272 | YES
29 | 1.68 | 32 | 53.76 | 12.1 | 5.64 | 11.5711 | YES
30 | 1.7 | 32.3 | 54.91 | 12.2 | 6.39 | 14.7125 | YES
31 | 1.82 | 24 | 43.68 | 12 | 6.44 | 15.3456 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2