## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-01-01
System Name: | SealRock Water District |  |  |  | 41-00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | Off | Off | Off | Off | Off | Off | Closed for Holiday
2 | Off | Off | 0.02 | 0.03 | Off | Off | 0.03
3 | Off | Off | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
4 | Off | Off | 0.02 | 0.03 | 0.03 | Off | 0.03
5 | Off | Off | 0.02 | Off | Off | Off | 0.02 / shut off w conductivity
6 | Off | Off | Off | Off | Off | Off | Conductivity
7 | Off | Off | Off | Off | Off | Off | Conductivity
8 | Off | Off | Off | Off | Off | Off | Conductivity
9 | Off | Off | Off | 0.03 | 0.02 | Off | 0.03
10 | Off | Off | 0.02 | 0.05 | 0.02 | 0.04 | 0.05
11 | Off | Off | 0.03 | 0.02 | 0.02 | Off | 0.03
12 | Off | Off | 0.03 | 0.03 | 0.02 | Off | 0.03
13 | Off | Off | 0.03 | 0.02 | 0.02 | Off | 0.03
14 | Off | Off | Off | Off | Off | Off | Off
15 | Off | Off | Off | Off | Off | Off | Off
16 | Off | Off | Off | Off | Off | Off | Off
17 | Off | Off | 0.02 | 0.02 | 0.02 | 0.003 | 0.03
18 | Off | Off | 0.02 | 0.02 | 0.02 | Off | 0.02
19 | Off | Off | 0.04 | 0.03 | 0.07 | 0.05 | 0.05
20 | Off | Off | 0.03 | 0.02 | 0.04 | Off | 0.04
21 | Off | Off | Off | Off | Off | Off | Off
22 | Off | Off | Off | Off | Off | Off | Off
23 | Off | Off | 0.05 | 0.02 | 0.02 | Off | 0.05
24 | Off | Off | 0.03 | 0.02 | 0.02 | 0.02 | 0.03
25 | Off | Off | 0.03 | 0.03 | 0.04 | 0.03 | 0.04
26 | Off | Off | 0.04 | 0.03 | 0.02 | Off | 0.04
27 | Off | Off |  |  |  |  | Del Computer Server Down
28 | Off | Off | Off | Off | Off | Off | Off
| Off | Off | Off | Off | Off | Off | Off
30 | Off | Off |  |  |  |  | Del Computer Server Down
31 | Off | Off |  |  |  |  | Del Computer Server Down
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: As of 01/26/2023 Del Server for our OHA Data was deemed out of service by Jacobs engineering. Repairs and software were brought back online 02/01/2023. Data was lost for those days of reporting 01/27-01/30-01/31 were gone. The plant did operate within state guidelines! |  |  |  |  | Larry Estes
[5 empty] | SIGNATURE:Larry Estes |  |  | DATE:02/02/2023
[5 empty] | PHONE #: ( 541 ) 961-7367 |  |  | CERT #:T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: | SealRock Water Dist |  | ID#: 4100798 |  | Month/Year: | 2023-01-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1
2 | 1.91 | 22.33 | 42.6503 | 12.52 | 6.17 | 13.1036 | YES
3 | 1.71 | 31.45 | 53.7795 | 11.91 | 6.9 | 17.8242 | YES
4 | 1.67 | 31.86 | 53.2062 | 11.61 | 7 | 18.7254 | YES
5 | 1.55 | 31.45 | 48.7475 | 11.4 | 6.51 | 15.848 | YES
6
7
8
9 | 1.17 | 37.42 | 43.7814 | 16.2 | 6.88 | 12.2529 | YES
10 | 0.9 | 37.72 | 33.948 | 11.62 | 7.1 | 17.7884 | YES
11 | 1.74 | 38.42 | 66.8508 | 15.49 | 7.03 | 14.5028 | YES
12 | 1.52 | 42.19 | 64.1288 | 14.06 | 7.23 | 16.7561 | YES
13 | 1.64 | 38.43 | 63.0252 | 13.9 | 6.96 | 15.5358 | YES
14
15
16
17 | 1.74 | 21.8 | 37.932 | 12.5 | 6.92 | 16.9965 | YES
18 | 1.89 | 67.83 | 128.1987 | 11.1 | 6.94 | 19.4272 | YES
19 | 1.54 | 35.16 | 54.1464 | 11.5 | 7.2 | 19.922 | YES
20 | 1.62 | 60.74 | 98.3988 | 11.44 | 6.97 | 18.6342 | YES
21 | 1.52 | 45.69 | 69.4488 | 11.49 | 7 | 18.5603 | YES
22
23 | 1.47 | 30.72 | 45.1584 | 11.68 | 6.97 | 18.0459 | YES
24 | 1.66 | 53.15 | 88.229 | 12.14 | 6.97 | 17.8901 | YES
25 | 1.5 | 52.35 | 78.525 | 11 | 6.87 | 18.2784 | YES
26 | 1.51 | 60.15 | 90.8265 | 12.34 | 6.97 | 17.3728 | YES
27 | [7 empty] | Del Server Down
28 | [7 empty] | Off
29 | [7 empty] | Off
30 | [7 empty] | Del Server Down
31 | [7 empty] | Del Server Down
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2