## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-02-01
System Name: | Seal Rock Water District |  |  | ID#: 41 | 00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
2 | OFF | OFF | 0.03 | 0.02 | OFF | OFF | 0.03
3 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | 0.03 | 0.02 | 0.02 | OFF | 0.03
7 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
8 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03
10 | OFF | OFF | 0.02 | 0.02 | 0.03 | OFF | 0.03
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | OFF | OFF | 0.03 | 0.02 | 0.03 | OFF | 0.03
14 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
15 | OFF | OFF | 0.03 | 0.03 | 0.03 | OFF | 0.03
16 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.03 | 0.03
17 | OFF | OFF | 0.04 | 0.04 | 0.05 | OFF | 0.05
18 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | OFF | OFF | OFF | 0.03 | 0.04 | OFF | 0.04
20 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
21 | OFF | OFF | 0.03 | 0.04 | 0.04 | OFF | 0.04
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | OFF | OFF | OFF | OFF | Salinity /Off
24 | OFF | OFF | OFF | OFF | OFF | OFF | Salinity /Off
25 | OFF | OFF | OFF | OFF | OFF | OFF | Salinity /Off
26 | OFF | OFF | OFF | OFF | OFF | OFF | Salinity /Off
27 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
28 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
29
30
31
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | YES | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | YES | YES |  | YES
Notes: |  |  |  |  | PRINTED NAME: Larry Estes
[5 empty] | SIGNATURE: Larry Estes |  |  | DATE:03/01/2023
[5 empty] | PHONE #: ( 541 ) 961-7367 |  |  | CERT #:T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- :C
System Name: | SealRock Water Dist. |  | ID#: 41 | 00798 | Month/Year: | 2023-02-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.54 | 35.21 | 54.2234 | 8.81 | 7.23 | 24.0392 | YES
2 | 1.48 | 74.26 | 109.9048 | 9.36 | 7.19 | 22.6965 | YES
3 | 1.37 | 60.44 | 82.8028 | 9.3 | 7.1 | 21.8032 | YES
4 | [7 empty] | OFF
5 | [7 empty] | OFF
6 | 1.32 | 60.73 | 80.1636 | 10.8 | 7.15 | 19.9961 | YES
7 | 1.39 | 26.32 | 36.5848 | 11.5 | 7.3 | 20.2844 | YES
8 | 1.44 | 64.27 | 92.5488 | 11.4 | 7.2 | 19.8297 | YES
9 | 1.37 | 43.27 | 59.2799 | 11.7 | 7.26 | 19.7007 | YES
10 | 1.39 | 38.32 | 53.2648 | 11.2 | 7.39 | 21.3482 | YES
11 | [7 empty] | OFF
12 | [7 empty] | OFF
13 | 1.52 | 49.03 | 74.5256 | 11.7 | 7.26 | 20.0335 | YES
14 | 1.49 | 29.44 | 43.8656 | 11.3 | 7.41 | 21.5994 | YES
15 | 1.48 | 30.95 | 45.806 | 10.86 | 7.43 | 22.3671 | YES
16 | 1.53 | 61.64 | 94.3092 | 9.99 | 7.42 | 23.7457 | YES
17 | 1.45 | 56 | 81.2 | 9.2 | 7.34 | 24.1066 | YES
18 | [7 empty] | OFF
19 | 1.4 | 36.24 | 50.736 | 9.25 | 7.37 | 24.1455 | YES
20 | 1.75 | 29.11 | 50.9425 | 10.87 | 7.45 | 23.2103 | YES | OFF
21 | 1.76 | 49.85 | 87.736 | 11.92 | 7.41 | 21.3765 | YES
22 | 1.84 | 24.22 | 44.5648 | 11.83 | 7.41 | 21.6982 | YES
23 | [7 empty] | OFF/Salinity
24 | [7 empty] | OFF/Salinity
25 | [7 empty] | OFF/Salinity
26 | [7 empty] | OFFSalinity
27 | 1.67 | 32.82 | 54.8094 | 10.51 | 7.39 | 23.0619 | YES
28 | 1.69 | 30.47 | 51.4943 | 9.49 | 7.26 | 23.6219 | YES
29
30
31
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2