## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-03-01
System Name: | SealRock Water District |  |  | ID#: 41 | 00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | OFF | OFF | 0.03 | 0.03 | 0.02 | 0.02 | 0.03
2 | OFF | OFF | 0.01 | 0.01 | OFF | OFF | 0.01
3 | OFF | OFF | 0.01 | 0.02 | OFF | OFF | 0.02
4 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
5 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
6 | OFF | OFF | 0.02 | 0.04 | 0.02 | 0.04 | 0.04
7 | OFF | OFF | 0.01 | 0.01 | 0.01 | 0.01 | 0.01
8 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
9 | OFF | OFF | 0.02 | 0.03 | 0.03 | 0.05 | 0.05
10 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
11 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
12 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
13 | OFF | OFF | 0.02 | 0.02 | 0.03 | 0.02 | 0.03
14 | OFF | OFF | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
15 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
16 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
17 | OFF | OFF | 0.02 | 0.02 | OFF | OFF | 0.02
18 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
19 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
20 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
21 | OFF | OFF | 0.01 | 0.01 | 0.01 | OFF | 0.01
22 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
23 | OFF | OFF | 0.02 | 0.02 | 0.02 | OFF | 0.02
24 | OFF | OFF | 0.02 | 0.01 | 0.01 | OFF | 0.02
25 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
26 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
27 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
28 | OFF | OFF | OFF | OFF | OFF | OFF | OFF
29 | OFF | OFF | OFF | 0.03 | 0.01 | OFF | 0.03
30 | OFF | OFF | 0.03 | 0.02 | 0.03 | OFF | 0.03
31 | OFF | OFF | 0.01 | 0.01 | 0.02 | OFF | 0.02
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | Larry Estes
[5 empty] | SIGNATURE:Larry Estes |  |  | DATE:03/31/2023
[5 empty] | PHONE #: ( 541 ) 961 7367 |  |  | CERT #:T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : C
System Name: | Seal Rock Water District |  | ID#: 41- | 00798 | Month/Year: | 2023-03-01 | Disinfection Giardia Log Inactiv: | 0.5
l
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.77 | 52.36 | 92.6772 | 9.39 | 7.19 | 23.4094 | YES
2 | 1.57 | 56.99 | 89.4743 | 9.46 | 7.1 | 22.0672 | YES
3 | 1.71 | 61.94 | 105.9174 | 9.48 | 7.08 | 22.2326 | YES
4 | 1.54 | 27.01 | 41.5954 | 10.09 | 7.03 | 20.5894 | YES
5 | [7 empty] | off
6 | 1.51 | 35.45 | 53.5295 | 10.38 | 7.2 | 21.3665 | YES
7 | 1.49 | 55.09 | 82.0841 | 10.2 | 7.3 | 22.344 | YES
8 | 1.46 | 55.2 | 80.592 | 10.1 | 7.3 | 22.4159 | YES
9 | 1.56 | 54.9 | 85.644 | 10.2 | 7.2 | 21.7433 | YES
10 | 1.47 | 55.1 | 80.997 | 10.2 | 7.2 | 21.5238 | YES
11 | [7 empty] | off
12 | 1.44 | 23.45 | 33.768 | 10 | 7.3 | 22.5136 | YES
13 | 1.42 | 41.05 | 58.291 | 10.6 | 7.3 | 21.5908 | YES
14 | 1.53 | 3607 | 5518.71 | 11.5 | 7.3 | 20.6051 | YES
15 | 1.54 | 40.1 | 61.754 | 11.3 | 7.1 | 19.4946 | YES
16 | 1.56 | 51.49 | 80.3244 | 11.55 | 7.2 | 19.9016 | YES
17 | 1.56 | 41.91 | 65.3796 | 11.21 | 7.2 | 20.3485 | YES
18 | 1.48 | 20.82 | 30.8136 | 11.75 | 7.26 | 19.8792 | YES
19
20 | 1.56 | 21.47 | 33.4932 | 11.95 | 7.4 | 20.7871 | YES
21 | 1.59 | 31.45 | 50.0055 | 12.2 | 7.2 | 19.1412 | YES
22 | 1.56 | 38.68 | 60.3408 | 11.9 | 7.29 | 20.0706 | YES
23 | 1.54 | 62.78 | 96.6812 | 11.8 | 7.31 | 20.2979 | YES
24 | 0.9 | 64.18 | 57.762 | 11.2 |  | 3.1397 | YES
25 | [7 empty] | off
26 | [7 empty] | off
27 | [7 empty] | lics prob- off
28 | [7 empty] | Del prob-off
29 | 1.23 | 64.12 | 78.8676 | 11.4 | 7.23 | 19.5734 | YES
30 | 1.03 | 64.15 | 66.0745 | 12 | 7.21 | 18.2866 | YES
31 | 1.26 | 64.01 | 80.6526 | 12.03 | 7.28 | 19.1801 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2