## Turbidity and CTs
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | County: | Lincoln
Slow Sand, Membrane, Diatomaceous Earth Filtration, or Unfiltered Systems | [6 empty] | Month/Year: | 2023-05-01
System Name: | Seal Rock Water District |  |  | ID#: 41 - | 00798 |  | WTP : TP - | C
Day | 12 AM [NTU] | 4 AM [NTU] | 8 AM [NTU] | NOON [NTU] | 4 PM [NTU] | 8 PM [NTU] | Highest Reading of the day 1 [NTU]
1 | Off | Off | 0.01 | 0.02 | 0.03 | 0.03 | 0.03
2 | Off | Off | 0.01 | 0.01 | 0.03 | 0.04 | 0.04
3 | Off | Off | 0.01 | 0.03 | 0.01 | 0.05 | 0.05
4 | Off | Off | 0.02 | 0.03 | 0.04 | 0.01 | 0.04
5 | Off | Off | 0.04 | 0.02 | 0.02 | 0.02 | 0.04
6 | Off | Off | Off | Off | Off | Off | Off
7 | Off | Off | Off | Off | Off | Off | Off
8 | Off | Off | 0.01 | 0.02 | 0.02 | 0.01 | 0.02
9 | Off | Off | 0.02 | 0.02 | 0.01 | 0.01 | 0.02
10 | Off | Off | 0.02 | 0.01 | 0.01 | 0.02 | 0.02
11 | Off | Off | 0.05 | 0.03 | 0.03 | off | 0.05
12 | Off | Off | 0.03 | 0.02 | 0.02 | Off | 0.03
13 | Off | Off | Off | Off | Off | Off | Off
14 | Off | Off | Off | Off | Off | Off | Off
15 | Off | Off | 0.02 | 0.03 | 0.02 | 0.02 | 0.03
16 | 0.02 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03
17 | Off | Off | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
18 | Off | Off | Off | Off | Off | Off | Off
19 | Off | Off | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
20 | Off | Off | Off | Off | Off | Off | Off
21 | Off | Off | Off | Off | Off | Off | Off
22 | Off | Off | 0.01 | 0.03 | 0.02 | 0.03 | 0.03
23 | Off | Off | 0.01 | 0.03 | 0.02 | Off | 0.03
24 | Off | Off | 0.02 | 0.03 | 0.01 | 0.02 | 0.03
25 | Off | Off | 0.03 | 0.02 | 0.02 | 0.01 | 0.03
26 | Off | Off | 0.02 | 0.03 | 0.02 | Off | 0.03
27 | Off | Off | Off | Off | Off | Off | Off
28 | Off | Off | Off | Off | Off | Off | Off
29 | Off | Off | 0.02 | 0.02 | 0.02 | 0.02 | 0.02
30 | 0.02 | 0.02 | 0.04 | 0.02 | 0.02 | 0.02 | 0.02
31 | 0.01 | 0.02 | 0.03 | 0.02 | 0.04 | 0.02 | 0.04
Slow Sand/Membrane/DE Filtration/Unfiltered |  |  |  |  | Monthly Summary (Answer Yes or No)
95% of daily turbidity readings ≤ 1 NTU? 2 |  |  |  | Yes | CT's met everyday? (see back) |  | All Cl2 residual at entry point ≥ 0.2 mg/l?
All daily turbidity readings ≤ 5 NTU? |  |  |  | Yes | Yes |  | Yes
Notes: |  |  |  |  | PRINTED NAME:Larry Estes
[5 empty] | Larry Estes |  |  | DATE:May 2023
[5 empty] | PHONE #: (541) 961-7367 |  |  | CERT #:T-09229
1 Including continuous NTU data, if applicable, for optimization recording purposes. Compliance values in columns 12 AM through 8 PM may not
correspond to continuous readings' maximum. 2 Filtered systems only.
PAGE 1 of 2
OHA - Drinking Water Services - Surface Water Quality Data Form | [6 empty] | WTP- : | C
System Name: | SealRock Water Dist |  | ID#: 41 | 00798 | Month/Year: | 2023-05-01 | Disinfection Giardia Log Inactiv: | 0.5
Date / Time | Minimum Cl2 Residual at 1st User ( C ) 3 | Contact Time (T) | Actual CT | Temp | pH | Required CT | CT Met? 3 | Peak Hourly Demand Flow
| [ppm or mg/L] | [minutes] | C X T | [° C] |  | formula | Yes / No | [GPM]
1 | 1.12 | 43.34 | 48.5408 | 15.12 | 7.45 | 16.1843 | YES
2 | 1.15 | 19.53 | 22.4595 | 15.24 | 7.54 | 16.6558 | YES
3 | 0.9 | 22.34 | 20.106 | 14.98 | 7.6 | 16.8413 | YES
4 | 0.8 | 20.07 | 16.056 | 14.85 | 7.42 | 15.7133 | YES
5 | 0.67 | 26.07 | 17.4669 | 14.11 | 7.5 | 16.7539 | YES
6 | 0.72 | 23.37 | 16.8264 | 15.6 | 7.73 | 16.6125 | YES
7
8 | 0.98 | 47.45 | 46.501 | 14.48 | 7.35 | 16.0185 | YES
9 | 1.01 | 47.65 | 48.1265 | 14.31 | 7.5 | 17.1837 | YES
10 | 0.99 | 48.03 | 47.5497 | 14.9 | 7.96 | 19.5358 | YES
11 | 0.88 | 48.43 | 42.6184 | 15.26 | 7.9 | 18.4257 | YES
12 | 0.81 | 59.38 | 48.0978 | 15.71 | 7.6 | 15.8784 | YES
13 | 0.75 | 59.85 | 44.8875 | 16.1 | 7.29 | 13.6953 | YES
14
15 | 0.81 | 46.02 | 37.2762 | 16.15 | 7.85 | 16.914 | YES
16 | 0.79 | 49.42 | 39.0418 | 17.4 | 7.9 | 15.8171 | YES
17 | 0.84 | 41.22 | 34.6248 | 17.7 | 7.93 | 15.7665 | YES
18 | 0.81 | 40.4 | 32.724 | 18.3 | 7.94 | 15.1522 | YES
19 | 0.91 | 76.99 | 70.0609 | 17.9 | 7.71 | 14.4537 | YES
20 | 0.71 | 29.22 | 20.7462 | 17.6 | 7.64 | 14.0438 | YES
21
22 | 0.84 | 44.17 | 37.1028 | 17.16 | 7.57 | 14.3027 | YES
23 | 0.84 | 32.33 | 27.1572 | 17.49 | 7.9 | 15.8122 | YES
24 | 0.9 | 51.82 | 46.638 | 16.2 | 7.8 | 16.7192 | YES
25 | 0.92 | 40.47 | 37.2324 | 17.2 | 7.85 | 15.97 | YES
26 | 0.89 | 50.76 | 45.1764 | 17.5 | 7.81 | 15.3708 | YES
27 | 0.83 | 19.26 | 15.9858 | 18.1 | 7.76 | 14.3969 | YES
28
29 | 0.95 | 51.34 | 48.773 | 17.18 | 7.78 | 15.6354 | YES
30 | 0.88 | 27.83 | 24.4904 | 17.8 | 7.2 | 11.9939 | YES
31 | 0.81 | 28.2 | 22.842 | 17.87 | 7.3 | 12.2923 | YES
3 If Cl2 at entry point < 0.2 mg/l or CT not met, notify DWS within 24 hours. | [6 empty] | Revised July 2018
Return by 10th of following month by email, fax, or mail to: dwp.dmce@state.or.us; 971-673-0694; or Drinking Water Services, PO Box 14350, Portland, OR 97293-0350
PAGE 2 of 2